## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay (mins) | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
FR-TR-RD-078 | LDP | 4B1LDP | Controller Module No:2 damaged | NO DEFECTS_37 | 2023-06-07 | 11:00 | Alarm idicated from SCADA/BMS System | 80760 | due to Overload on Controller Module | Hardware | No | N/A | BMS team will be rectify | N/A | 2023-08-02 | 11:00
FR-TR-RD-102 | CBS | 6E1CBS | INC_20230716_001:-CBS lights moduels damged | CBS Module | 2023-07-16 | 8:00 | Caertaking team | 24959.9667 | [manufacturing DEFECTS] | Hardware | No | N/A | Letter has been sent to Supplier | N/A | 2023-08-02 | 8:00 |  |  |  | 213
FR-TR-RD-103 | MDB | 6F1MDB | INC_20230716_002:-Some DMF not working ,Some Indicator light not working, Door handel damge,Tag missing , reported to supplier and waiting them to visit site | NO DEFECTS_16 | 2023-07-16 | 8:00 | Caertaking team | 24959.9667 | Damage | Hardware | No | N/A | Letter has been sent to Supplier | N/A | 2023-08-02 | 8:00
FR-TR-RD-105 | CPM | 6G1CPM | INC_20230610_001:- Return flow shown (LOI Comm Error) | NO DEFECTS_19 | 2023-06-10 | 17:50 | Caertaking team | 75620 | Montioring CPM to find the flow as Flow meter display only shown error | Hardware | No | N/A | Letter has been sent to Supplier | N/A | 2023-08-02 | 17:50
FR-TR-RD-107 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-01 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 89640 | Door is closed but appear as open in ACID, Controller damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:00 |  |  |  | 201
FR-TR-RD-108 | ACID | 4E1ACID | Door is closed at site, still appear as open in system - | ACID Configuration | 2023-06-01 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 89640 | Door is closed but appear as open in ACID, Controller damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:00 |  |  |  | 201
FR-TR-RD-109 | CCTV | 4E1CCTV | image not clear | NO DEFECTS_3 | 2023-06-01 | 7:00 | Physical inspection lead to failure identification | 89880 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 7:00
FR-TR-RD-110 | ACID | 4E1ACID | Door is closed at site, still appear as open in system - | NO DEFECTS_9 | 2023-06-02 | 8:00 | Found alarm in ACID, lead to inspection of failure identification | 88320 | Control Board damaged | Hardware | No | N/A | Raised PR for maintenance | N/A | 2023-08-02 | 8:00
FR-TR-RD-111 | ACID | 4E1ACID | Door is closed at site, still appear as open in system, appears intrusion | NO DEFECTS_9 | 2023-06-02 | 8:00 | Found alarm in ACID, lead to inspection of failure identification | 88320 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-112 | LCS | 4E1LCS | Lights are not turning ON & OFF as per schedule | NO DEFECTS_36 | 2023-06-04 | 5:00 | Physical inspection lead to failure identification | 85800 | Programming Issue | Software | No | N/A | Informed to BMS team to rectify | N/A | 2023-08-02 | 5:00
FR-TR-RD-113 | FCU | 4E1FCU | Not working | FCU-Controller | 2023-06-08 | 11:00 | Found alarm in BMS, lead to inspection of failure identification | 79320 | Control Board damaged | Hardware | No | N/A | Raised PR for maintenance | N/A | 2023-08-02 | 11:00 |  |  |  | 203
FR-TR-RD-114 | BMS | 4E1BMS | BMS server communication set to failed | NO DEFECTS_22 | 2023-06-08 | 19:58 | Found alarm in Scada, lead to inspection of failure identification | 78244 | Scada Programming Base line issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 19:58
FR-TR-RD-115 | FDS | 4E1FDS | FACP PLC communication set to failed | NO DEFEC_30 | 2023-06-08 | 19:58 | Found alarm in Scada, lead to inspection of failure identification | 78244 | Scada Programming Base line issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 19:58
FR-TR-RD-116 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-13 | 14:30 | Found alarm in Scada, lead to inspection of failure identification | 71700 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 14:30
FR-TR-RD-117 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-13 | 14:30 | Found alarm in Scada, lead to inspection of failure identification | 71700 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 14:30
FR-TR-RD-118 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-13 | 14:30 | Found alarm in Scada, lead to inspection of failure identification | 71700 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 14:30
FR-TR-RD-119 | ACID | 4E1ACID | Lock is not getting open by access card | ACID Card reader issue | 2023-06-14 | 7:00 | Physical inspection lead to failure identification | 71160 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 7:00 |  |  |  | 200
FR-TR-RD-120 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 69600 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-121 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 69600 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-122 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 69600 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-123 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 69600 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-124 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 69600 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-125 | MDB | 4E1MDB | Power Shutdown | NO DEFECTS_16 | 2023-06-26 | 13:30 | Power Failure in station | 53100 | PLC is not giving the command to close the MDB outgoing breaker , and the UPS covers the power until the battery is drained | Software | No | N/A | Informed to Generatoe Supplier (Cumins) | N/A | 2023-08-02 | 13:30
FR-TR-RD-126 | FDS | 4E1FDS | Local trouble act Map fault data card 1 L3 | NO DEFEC_30 | 2023-07-02 | 6:00 | Found alarm in fire alarm, lead to inspection of failure identification | 45360 | Fire Alarm programming issue | Software | No | N/A | Informed to supplier (Zamil) | N/A | 2023-08-02 | 6:00
FR-TR-RD-127 | CHILLER | 4E1CHILLER | high pressure cutout, Chiller Compressor is getting OFF, | NO DEFECTS_4 | 2023-07-04 | 14:00 | Physical inspection lead to failure identification | 41520 | Condensing fan motors damaged | Hardware | No | N/A | Raised PR for spare parts | N/A | 2023-08-02 | 14:00
FR-TR-RD-128 | CHILLER | 4E1CHILLER | Communication Loss, Chiller Compressor is getting OFF, | NO DEFECTS_4 | 2023-07-04 | 14:00 | Physical inspection lead to failure identification | 41520 | Suction Pressure Transducer damaged | Hardware | No | N/A | Raised PR for spare parts | N/A | 2023-08-02 | 14:00
FR-TR-RD-129 | CCTV | 4D1CCTV | cameras are offline, Working with IP address, but have issue with ISM | ISM Programming Issue | 2023-06-01 | 8:00 | Found alarm in Scada, lead to the failure identification | 89760 | Appears offline in ISM | Software | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 8:00 |  |  |  | 209
FR-TR-RD-130 | CCTV | 4D1CCTV | cameras are offline, Working with IP address, but have issue with ISM | ISM Programming Issue | 2023-06-01 | 8:00 | Found alarm in Scada, lead to the failure identification | 89760 | Appears offline in ISM | Software | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 8:00 |  |  |  | 209
FR-TR-RD-131 | CHILLER | 4D1CHILLER | Blower motor damaged | NO DEFECTS_4 | 2023-06-01 | 10:00 | Physical inspection lead to the failure identification | 89520 | Required to replace motor | Hardware | No | N/A | Raised PR for spare part | N/A | 2023-08-02 | 10:00
FR-TR-RD-132 | CHILLER | 4D1CHILLER | Water Leakage from the Heater | NO DEFECTS_4 | 2023-06-04 | 14:00 | Physical inspection lead to the failure identification | 84720 | heater have internal leakage | Hardware | No | N/A | Raised PR for Supplier | N/A | 2023-08-02 | 14:00
FR-TR-RD-133 | ACID | 4D1ACID | Controller Issue | NO DEFECTS_9 | 2023-06-07 | 9:00 | Found alarm in Scada, lead to the failure identification | 81000 | Programming Issue | Software | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 9:00
FR-TR-RD-134 | ACID | 4D1ACID | Controller Issue | NO DEFECTS_9 | 2023-06-07 | 9:00 | Found alarm in Scada, lead to the failure identification | 81000 | Programming Issue | Software | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 9:00
FR-TR-RD-135 | FCU | 4D1FCU | Controller & PCB damged | FCU PCB | 2023-06-10 | 11:00 | Physical inspection lead to the failure identification | 76440 | Required to replace PCB & controller | Hardware | No | N/A | Raised PR for spare part | N/A | 2023-08-02 | 11:00 |  |  |  | 205
FR-TR-RD-136 | FCU | 4D1FCU | Controller & PCB damged | FCU PCB | 2023-06-10 | 11:00 | Physical inspection lead to the failure identification | 76440 | Required to replace PCB & controller | Hardware | No | N/A | Raised PR for spare part | N/A | 2023-08-02 | 11:00 |  |  |  | 205
FR-TR-RD-137 | BMS | 4D1BMS | BMS server communication set to failed | NO DEFECTS_22 | 2023-06-18 | 8:38 | Found alarm in Scada, lead to inspection of failure identification | 65204 | Scada Programming Base line issue | Software | No | N/A | Informed to supplier | N/A | 2023-08-02 | 8:38
FR-TR-RD-138 | FDS | 4D1FDS | FACP PLC communication set to failed | NO DEFEC_30 | 2023-06-18 | 8:38 | Found alarm in Scada, lead to inspection of failure identification | 65204 | Scada Programming Base line issue | Software | No | N/A | Informed to supplier | N/A | 2023-08-02 | 8:38
FR-TR-RD-139 | FS | 4D1FS | Day Tank Fuel Level Sensor not indicating fuel level in EVO panel | NO DEFECTS_32 | 2023-06-20 | 13:00 | Physical inspection lead to the failure identification | 61800 | Level Sensor communication issue | Software | No | N/A | Informed to supplier | N/A | 2023-08-02 | 13:00
FR-TR-RD-140 | CPM | 4D1-CPM | con 2, CPM is not working on VFD mode | NO DEFECTS_19 | 2023-06-21 | 16:00 | Physical inspection lead to the failure identification | 60000 | CPM programming issue | Software | No | N/A | Informed to supplier | N/A | 2023-08-02 | 16:00
FR-TR-RD-141 | ACID | 4D1ACID | Not getting open by access card | ACID Card reader issue | 2023-06-23 | 7:00 | Physical inspection lead to the failure identification | 58200 | Programming Issue | Software | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 7:00 |  |  |  | 200
FR-TR-RD-142 | ACID | 4D1ACID | Not getting open by access card | ACID Card reader issue | 2023-06-23 | 7:00 | Physical inspection lead to the failure identification | 58200 | Programming Issue | Software | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 7:00 |  |  |  | 200
FR-TR-RD-143 | BMS | 4D1BMS | BMS graphics not appearing, can't access equipment to check & rectify for any alarm | NO DEFECTS_22 | 2023-06-24 | 6:00 | Physical inspection lead to the failure identification | 56880 | Programming Issue | Software | No | N/A | Informed to BMS team | N/A | 2023-08-02 | 6:00
FR-TR-RD-144 | CCTV | 4D1CCTV | cameras are offline, Working with IP address, but have issue with ISM | ISM Programming Issue | 2023-06-24 | 20:52 | Found alarm in Scada, lead to the failure identification | 55096 | Appears offline in ISM | Software | No | N/A | Need to rectify from OCC | N/A | 2023-08-02 | 20:52 |  |  |  | 209
FR-TR-RD-145 | ACID | 4D1ACID | Door always appear as open, at site when it's closed also | NO DEFECTS_9 | 2023-06-26 | 6:23 | Found alarm in Scada, lead to the failure identification | 53954 | Acid Relay damaged | Hardware | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 6:23
FR-TR-RD-146 | ACID | 4D1ACID | Door always appear as open, at site when it's closed also | NO DEFECTS_9 | 2023-06-26 | 6:23 | Found alarm in Scada, lead to the failure identification | 53954 | Acid Relay damaged | Hardware | No | N/A | Informed to ICT team | N/A | 2023-08-02 | 6:23
FR-TR-RD-147 | CCTV | 4D1ACID | cameras are offline, Working with IP address, but have issue with ISM | ISM Programming Issue | 2023-06-27 | 13:47 | Found alarm in Scada, lead to the failure identification | 51626 | Appears offline in ISM | Software | No | N/A | Need to rectify from OCC | N/A | 2023-08-02 | 13:47 |  |  |  | 209
FR-TR-RD-148 | FCU | 4B1FCU | PCB not working (red color) | FCU PCB | 2023-06-01 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 89760 | PBC not working due to fuse | Hardware | No | N/A | PR raise and waiting for supplier to deliver | N/A | 2023-08-02 | 8:00 |  |  |  | 205
FR-TR-RD-149 | FCU | 4B1FCU | Tranformer burned | FCU Wrong Termination | 2023-06-01 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 89640 | due to wrong termination | Hardware | No | N/A | PR raise and waiting for supplier to deliver | N/A | 2023-08-02 | 9:00 |  |  |  | 206
FR-TR-RD-150 | FCU | 4B1FCU | PCB not working & ON/OFF swicth not working | FCU Wrong Termination | 2023-06-01 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 89640 | FCU selector swicth not working due to wrong wiring | Hardware | No | N/A | PR raise and waiting for supplier to deliver | N/A | 2023-08-02 | 9:00 |  |  |  | 206
FR-TR-RD-151 | FCU | 4B1FCU | FCU coil Leakage | NO DEFETCS_7 | 2023-06-01 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 89640 | water leaking from coil | Hardware | No | N/A | PR raise and waiting for supplier to deliver | N/A | 2023-08-02 | 9:00
FR-TR-RD-152 | FCU | 4B1FCU | PCB not working (red & Green color) | FCU PCB | 2023-06-01 | 11:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 89400 | PBC not working due to fuse damage | Hardware | No | N/A | PR raise and waiting for supplier to deliver | N/A | 2023-08-02 | 11:00 |  |  |  | 205
FR-TR-RD-153 | FCU | 4B1FCU | PCB not working (red color) | FCU PCB | 2023-06-01 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 89760 | PBC not working due to fuse | Hardware | No | N/A | PR raise and waiting for supplier to deliver | N/A | 2023-08-02 | 8:00 |  |  |  | 205
FR-TR-RD-154 | FCU | 4B1FCU | FCU Motor winding got damaged due to wrong termination | FCU Wrong Termination | 2023-06-01 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 89760 | Due to overload on motor | Hardware | No | N/A | PR raise and waiting for supplier to repair | N/A | 2023-08-02 | 8:00 |  |  |  | 206
FR-TR-RD-155 | SEXF | 4B1SEXF | SEF Motor winding got damaged | SEF Fan Motor | 2023-06-04 | 8:00 | Alarm idicated from SCADA/BMS System | 85440 | Due to MCC Contactor not give the Volt, due to L3 power failure. | Hardware | No | N/A | Sent motor to workshop for rewinding | N/A | 2023-08-02 | 8:00 |  |  |  | 212
FR-TR-RD-156 | MCC | 4B1MCC | contartor got damaged | MCC-Contractor | 2023-06-05 | 10:00 | Alarm idicated from SCADA/BMS System | 83760 | due to wrong termination | Hardware | No | N/A | need to Informed splier for cotactor | N/A | 2023-08-02 | 10:00 |  |  |  | 210
FR-TR-RD-157 | MCC | 4B1MCC | contartor got damaged | MCC-Contractor | 2023-06-05 | 10:00 | Alarm idicated from SCADA/BMS System | 83760 | due to wrong termination | Hardware | No | N/A | need to Informed splier for cotactor | N/A | 2023-08-02 | 10:00 |  |  |  | 210
FR-TR-RD-158 | CBS | 4B1CBS | SOU Module NO:1 damaged | NO DEFECTS_2 | 2023-06-08 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 79680 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair | N/A | 2023-08-02 | 8:00
FR-TR-RD-159 | CBS | 4B1CBS | SOU Module NO:8 damaged | NO DEFECTS_2 | 2023-06-08 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 79680 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair | N/A | 2023-08-02 | 8:00
FR-TR-RD-160 | CBS | 4B1CBS | SOU Module No:2 damaged | NO DEFECTS_2 | 2023-06-08 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 79560 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair | N/A | 2023-08-02 | 9:00
FR-TR-RD-161 | CBS | 4B1CBS | SOU Module NO:4 damaged | NO DEFECTS_2 | 2023-06-08 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 79560 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair | N/A | 2023-08-02 | 9:00
FR-TR-RD-162 | SEXF | 4B1SEXF | Maintenace alart for Dirty | NO DEFECTS_8 | 2023-06-11 | 6:00 | Alarm idicated from Fire Alarm System | 75600 | Due to dust accumlated on Smoke Detector | Hardware | No | N/A | Electrical team will be rectify | N/A | 2023-08-02 | 6:00
FR-TR-RD-163 | SEXF | 4B1SEXF | Maintenace alart for Dirty | NO DEFECTS_8 | 2023-06-11 | 9:00 | Alarm idicated from Fire Alarm System | 75240 | Due to dust accumlated on Smoke Detector | Hardware | No | N/A | Electrical team will be rectify | N/A | 2023-08-02 | 9:00
FR-TR-RD-164 | MCC | 4B1MCC | Contactor not working | MCC-Contractor | 2023-06-12 | 8:00 | Alarm idicated from SCADA/BMS System | 73920 | MCC Contactor not give the Volt, due to L3 power failure. | Hardware | No | N/A | need to Inform Meta team | N/A | 2023-08-02 | 8:00 |  |  |  | 210
FR-TR-RD-165 | FCU | 4B1FCU | Graphics not shown | NO DEFETCS_7 | 2023-06-13 | 7:00 | Alarm idicated from SCADA/BMS System | 72600 | FCU working fine but BMS system Graphics not shown | Software | No | N/A | Informed BMS team to rectify | N/A | 2023-08-02 | 7:00
FR-TR-RD-166 | CCTV | 4B1CCTV | Offline | NO DEFECTS_3 | 2023-06-18 | 9:00 | Monitoring from SCADA/ISM System | 65160 | Not Working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:00
FR-TR-RD-167 | CCTV | 4B1CCTV | Not configure | ICT Programming Issue | 2023-06-18 | 9:00 | Monitoring from SCADA/ISM System | 65160 | Not Working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:00 |  |  |  | 208
FR-TR-RD-168 | CCTV | 4B1CCTV | Offline | NO DEFECTS_3 | 2023-06-18 | 9:00 | Monitoring from SCADA/ISM System | 65160 | Not Working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:00
FR-TR-RD-169 | CPM | 4B1CPM | PCB not working (Green color) | NO DEFECTS_19 | 2023-06-20 | 11:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 62040 | PBC not working due to cable lose connection | Hardware | No | N/A | Electrical team will be rectify | N/A | 2023-08-02 | 11:00
FR-TR-RD-170 | MDB | 4B1MDB | Remote mode not working | NO DEFECTS_16 | 2023-06-22 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 59520 | BMS cable wrong connection | Hardware | No | N/A | BMS team will be rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-171 | FDS | 4B1FDS | Map Fault DataCard1 L7 | NO DEFEC_30 | 2023-07-03 | 8:00 | Alarm idicated from Fire Alarm System | 43680 | Due to not properly installed | Hardware | No | N/A | Fire alarm team will be rectify | N/A | 2023-08-02 | 8:00
FR-TR-RD-172 | UPS | 4B1UPS | Fan not working | NO DEFECTS_6 | 2023-07-14 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 27720 | Due to Fan replacement | Hardware | No | N/A | BMS team will be rectify | N/A | 2023-08-02 | 9:00
FR-TR-RD-173 | ACID | 4C1ACID | Not opening with Card | ACID Card reader issue | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 89680 | No communication | Software | No | N/A | Informed to ICT team to rectify | N/A | 2023-08-02 | 8:40 |  |  |  | 200
FR-TR-RD-174 | ACID | 4C1ACID | working with card but not opening frm system | ACID Configuration | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 89680 | No communication | Software | No | N/A | Informed to ICT team to rectify | N/A | 2023-08-02 | 8:40 |  |  |  | 201
FR-TR-RD-175 | ACID | 4C1ACID | Alarm occuring all the time | ACID Configuration | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 89680 | No communication | Software | No | N/A | Informed to ICT team to rectify | N/A | 2023-08-02 | 8:40 |  |  |  | 201
FR-TR-RD-176 | ACID | 4C1ACID | Not opening with Card | ACID Card reader issue | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 89680 | No communication | Software | No | N/A | Informed to ICT team to rectify | N/A | 2023-08-02 | 8:40 |  |  |  | 200
FR-TR-RD-177 | ACID | 4C1ACID | Not opening with Card | ACID Card reader issue | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 89680 | No communication | Software | No | N/A | Informed to ICT team to rectify | N/A | 2023-08-02 | 8:40 |  |  |  | 200
FR-TR-RD-178 | ACID | 4C1ACID | Not opening with Card & system | ACID Configuration | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 89680 | No communication | Software | No | N/A | Informed to ICT team to rectify | N/A | 2023-08-02 | 8:40 |  |  |  | 201
FR-TR-RD-179 | CCTV | 4C1CCTV | No configuration | Loss of communication | 2023-06-01 | 7:23 | Alarm indicated in Scada/ISM System | 89834 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23 |  |  |  | 211
FR-TR-RD-180 | CCTV | 4C1CCTV | Camera not working | Loss of communication | 2023-06-01 | 7:23 | Alarm indicated in Scada/ISM System | 89834 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23 |  |  |  | 211
FR-TR-RD-181 | CCTV | 4C1CCTV | Camera not working | NO DEFECTS_3 | 2023-06-01 | 7:23 | Alarm indicated in Scada/ISM System | 89834 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23
FR-TR-RD-182 | CCTV | 4C1CCTV | Camera not working | NO DEFECTS_3 | 2023-06-01 | 7:23 | Alarm indicated in Scada/ISM System | 89834 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23
FR-TR-RD-183 | CCTV | 4C1CCTV | Camera not working | NO DEFECTS_3 | 2023-06-02 | 7:23 | Alarm indicated in Scada/ISM System | 88394 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23
FR-TR-RD-184 | CCTV | 4C1CCTV | Camera not working | NO DEFECTS_3 | 2023-06-02 | 7:23 | Alarm indicated in Scada/ISM System | 88394 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23
FR-TR-RD-185 | CCTV | 4C1CCTV | Camera not working | Loss of communication | 2023-06-02 | 7:23 | Alarm indicated in Scada/ISM System | 88394 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23 |  |  |  | 211
FR-TR-RD-186 | CCTV | 4C1CCTV | Camera not working | Loss of communication | 2023-06-02 | 7:23 | Alarm indicated in Scada/ISM System | 88394 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV | N/A | 2023-08-02 | 7:23 |  |  |  | 211
FR-TR-RD-187 | FCU | 4C1FCU | Motor damaged | FCU Motor | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 88320 | Due to running | Hardware | No | N/A | Informed supplier to change the Motor | N/A | 2023-08-02 | 8:00 |  |  |  | 204
FR-TR-RD-188 | FCU | 4C1FCU | Blower damaged | NO DEFECTS_7 | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 88320 | Due to running | Hardware | No | N/A | Informed supplier to change the Blower | N/A | 2023-08-02 | 8:00
FR-TR-RD-189 | FCU | 4C1FCU | Motor Not running on AUTO | FCU Motor | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 88320 | Motor start problem | Hardware | No | N/A | informed supplier to check | N/A | 2023-08-02 | 8:00 |  |  |  | 204
FR-TR-RD-190 | FCU | 4C1FCU | Fan gets trippped | NO DEFECTS_7 | 2023-06-04 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 85440 | Due to Over load | Hardware | No | N/A | informed electrical team to check | N/A | 2023-08-02 | 8:00
FR-TR-RD-191 | CPM | 4C1CPM | Pumps not running on VFD | NO DEFECTS_19 | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 82634 | Not working due to lost of Communication | Software | No | N/A | informed electrical team to check | N/A | 2023-08-02 | 7:23
FR-TR-RD-192 | CPM | 4C1CPM | Pumps not running on VFD | NO DEFECTS_19 | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 82634 | Not working due to lost of Communication | Software | No | N/A | informed electrical team to check | N/A | 2023-08-02 | 7:23
FR-TR-RD-193 | CPM | 4C1CPM | Pumps not running on VFD | NO DEFECTS_19 | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 82634 | Not working due to lost of Communication | Software | No | N/A | informed electrical team to check | N/A | 2023-08-02 | 7:23
FR-TR-RD-194 | MCC | 4C1MCC | contartor got damaged | MCC-Contractor | 2023-06-12 | 10:00 | Alarm idicated from SCADA/BMS System | 73680 | due to wrong termination | Hardware | No | N/A | Informed supplier to change the Contactor | N/A | 2023-08-02 | 10:00 |  |  |  | 210
FR-TR-RD-195 | MCC | 4C1MCC | contartor got damaged | MCC-Contractor | 2023-06-12 | 10:00 | Alarm idicated from SCADA/BMS System | 73680 | due to wrong termination | Hardware | No | N/A | Informed supplier to change the Contactor | N/A | 2023-08-02 | 10:00 |  |  |  | 210
FR-TR-RD-196 | CPM | 4C1CPM | Pumps not running | NO DEFECTS_19 | 2023-06-16 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 68234 | Not working due to electrical Problem | Hardware | No | N/A | informed electrical team to check | N/A | 2023-08-02 | 7:23
FR-TR-RD-197 | AHUS | 4C1AHUS | Tripping while Running | NO DEFECTS_1 | 2023-06-06 | 7:00 | Alarm idicated from SCADA/BMS System | 82680 | Due to overload | Hardware | No | N/A | Informed to Electrical team to check | N/A | 2023-08-02 | 7:00
FR-TR-RD-198 | AHUS | 4C1AHUS | Abnormal Sound in Motor | NO DEFECTS_1 | 2023-06-08 | 7:00 | Alarm idicated from SCADA/BMS System | 79800 | Due to unbalance od shaft | Hardware | No | N/A | Informed to Supplier | N/A | 2023-08-02 | 7:00
FR-TR-RD-199 | AHUS | 4G1AHUS | UNUSUAL NOISE FROM AHU SUPPLY BLOWER | NO DEFECTS_1 | 2023-02-06 | 8:30 | Found during physical inspection | 255300 | Required to confirm by supplier | Hardware | No | N/A | PR RAISED TO SUPPILER | N/A | 2023-08-02 | 8:30
FR-TR-RD-200 | DWS | 4G1DWS | WATER LEAKAGE FROM INSIDE THE PUMP INTERNAL SEAL ISSUE | NO DEFECTS_5 | 2023-03-06 | 10:00 | Found during physical inspection | 214800 | Required to confirm by supplier | Hardware | No | N/A | PR RAISED TO SUPPILER | N/A | 2023-08-02 | 10:00
FR-TR-RD-201 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-06 | 16:00 | Found alarm in ISM, lead to inspection of failure identification | 81600 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 16:00 |  |  |  | 208
FR-TR-RD-202 | ACID | 4G1ACID | Configuration Issue | ACID Configuration | 2023-06-12 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 73800 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:00 |  |  |  | 201
FR-TR-RD-203 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-204 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-205 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-206 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | This camera repeating two times in ISM, and its offline | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-207 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-208 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-209 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-210 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-211 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-212 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 70860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 9:30 |  |  |  | 208
FR-TR-RD-213 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 10:00 | Found alarm in ISM, lead to inspection of failure identification | 70800 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 10:00 |  |  |  | 208
FR-TR-RD-214 | CCTV | 4G1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-14 | 10:00 | Found alarm in ISM, lead to inspection of failure identification | 70800 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 10:00 |  |  |  | 208
FR-TR-RD-215 | FCU | 4G1FCU | Remaining to configure in BMS work station | NO DEFECTS_7 | 2023-06-14 | 11:00 | Found during physical inspection | 70680 | The fcu is installing later that’s why still remaining to programming in BMS Work station by JCI TEAM | Hardware | NO | N/A | Informed BMS team to rectify | N/A | 2023-08-02 | 11:00
FR-TR-RD-216 | BMS | 4G1BMS | Scada Base line programming issue | NO DEFECTS_22 | 2023-06-18 | 8:00 | Found alarm in Scada, lead to inspection of failure identification | 65280 | BMS-Server Communication faild- and the error is SCADA Programming Base line issue | Software | NO | N/A | SCADA Baseline update ongoing | N/A | 2023-08-02 | 8:00
FR-TR-RD-217 | FCU | 4G1FCU | Scada Base line programming issue | NO DEFECTS_7 | 2023-06-18 | 8:00 | Found alarm in Scada, lead to inspection of failure identification | 65280 | BMS-Server Communication faild- and the error is SCADA Programming Base line issue | Software | NO | N/A | SCADA Baseline update ongoing | N/A | 2023-08-02 | 8:00
FR-TR-RD-218 | FRCP | 4G1FRCP | WATER LEAKAGE FROM INSIDE THE PUMP INTERNAL SEAL ISSUE | NO DEFECTS_31 | 2023-06-24 | 9:00 | Found during physical inspection | 56520 | Required to confirm by supplier | Hardware | NO | N/A | PR RAISED TO SUPPILER | N/A | 2023-08-02 | 9:00
FR-TR-RD-219 | ES | 4G1ES | General faults | NO DEFECTS_28 | 2023-06-24 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 56520 | Suddenly stop with faults error / Required to confirm by supplier | Hardware | NO | N/A | Informed to OTIS Team to Rectify | N/A | 2023-08-02 | 9:00
FR-TR-RD-220 | ACID | 4G1ACID | Always open, appears intrusion | NO DEFECTS_9 | 2023-07-12 | 8:30 | Found alarm in Scada, lead to inspection of failure identification | 30660 | Programming Issue | Software | NO | N/A | Informed to ICT Team to Rectify | N/A | 2023-08-02 | 8:30
FR-TR-RD-221 | ACID | 4G1ACID | DOOR IS OFFLINE | ACID Configuration | 2023-06-12 | 8:30 | Found alarm in Scada, lead to inspection of failure identification | 73860 | Door is closed but appear as open in ACID | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:30 |  |  |  | 201
FR-TR-RD-222 | ACID | 4G1ACID | Always open, appears intrusion | NO DEFECTS_9 | 2023-06-12 | 8:30 | Found alarm in Scada, lead to inspection of failure identification | 73860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:30
FR-TR-RD-223 | ACID | 4G1ACID | Door is offline | ACID Configuration | 2023-06-12 | 8:30 | Found alarm in Scada, lead to inspection of failure identification | 73860 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:30 |  |  |  | 201
FR-TR-RD-224 | INTERCOM | 4G1INTERCOM | INTERCOM IS OFFLINE | NO DEFECTS_35 | 2023-06-12 | 8:30 | Found alarm in Scada, lead to inspection of failure identification | 73860 | Required to confirm by supplier | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-08-02 | 8:30
TR-FRCS-2023-0083 | TRV | 4C2TRV | 4C2 Exit 1 Travelator02 component Damage Detected | NO DEFECTS_38 | 2023-07-08 | 14:29 | travelator second set towards exit 1 with unusual sound and found chipped rubber | 35702 | travelator second set towards exit 1 with unusual sound and found chipped rubber | Hardware | No | N/A | Expecting response for EIR | N/A | 2023-08-02 | 14:29
TR-FRCS-2023-0075 | GEN | ITPS4.4GEN | ITPS 4.4 DG not working properly. Fire watcher of ITPS 4.4 informed, DG is getting stopped after 10 min. | NO DEFECTS_17 | 2023-07-05 | 12:59 | This was in accordance with message received from sentinel. | 24241 | Investigation was performed on lighting circuits to illuminate lights, | Hardware | No | N/A | Change the busted bulb 4pcs | N/A | 2023-07-05 | 12:59 | 2023-07-22 | 15:00
TR-FRCS-2023-0083 | TRV | 4C2TRV | 4C2 Exit 1 Travelator02 component Damage Detected | NO DEFECTS_38 | 2023-07-08 | 14:29 | travelator second set towards exit 1 with unusual sound and found chipped rubber | 35702 | travelator second set towards exit 1 with unusual sound and found chipped rubber | Hardware | No | N/A | Expecting response for EIR | N/A | 2023-08-02 | 14:29
FR-TR-RD-252 | AHUS | 6D2AHUS | AHU's V-belt Damaged | NO DEFECTS_1 | 27-07-2023 | 7:35 | Caretaking team found | 295 | caretaking team start corrective maintence | harware | no | N/A | AHU's V-belt damaged due to overdue (Prolong used) And new filter replaced | N/A | 27-07-2023 | 7:35 | 27-07-2023 | 12:30
FR-TR-RD-084 | AHUS | 4C1AHUS | AHU BELT BROKEN | NO DEFECTS_1 | 2023-06-20 | 10:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 30 | DUE TO RUNNING | Hardware | No | N/A | Change belt | N/A | 2023-06-20 | 11:00 | 2023-06-20 | 11:30
FR-TR-RD-085 | FDS | 4C1FDS | dirty detector | NO DEFEC_30 | 2023-06-22 | 6:00 | Alarm idicated from SCADA/BMS System | 30 | due to dust | Hardware | No | N/A | clean the detector | N/A | 2023-06-22 | 11:00 | 2023-06-22 | 11:30
FR-TR-RD-086 | FDS | 4C1FDS | dirty detector | NO DEFEC_30 | 2023-06-23 | 6:00 | Alarm idicated from SCADA/BMS System | 30 | due to dust | Hardware | No | N/A | clean the detector | N/A | 2023-06-23 | 9:00 | 2023-06-23 | 9:30
FR-TR-RD-087 | FDS | 4C1FDS | dirty detector | NO DEFEC_30 | 2023-06-25 | 6:00 | Alarm idicated from SCADA/BMS System | 30 | due to dust | Hardware | No | N/A | clean the detector | N/A | 2023-06-25 | 10:00 | 2023-06-25 | 10:30
FR-TR-RD-090 | FCU | 4C1FCU | AHU BELT BROKEN | NO DEFECTS_7 | 2023-06-04 | 11:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 30 | DUE TO RUNNING | Hardware | No | N/A | Change belt | N/A | 2023-06-04 | 12:00 | 2023-06-04 | 12:30
TR-FRCS-2023-0051 | UPS | 6H2UPS | LPS & DG non-functional due to potential UPS failure Asset: ELF / UPSR-INM-ELF-UPS -- 11:28 Nominal service 4A1-4G1-6A1-6H2 deactivated, AS all LPS of L6 failed and DG at 6H2 is not working 11:29 Temporary service 4A1-4G1-6A1-6G2 activated due to potential UPS failure at 6H2 12:16 TS 3 suspended and Nominal service 4A1-4G1-6A1-6H2 activated with 9 Line 6 trains and 8 Line 4 trains, 30min after the confirmation that all LPS are healthy . | UPS Power Damage | 2023-06-28 | 11:00 | Physical detection | 34 | DG at 6H2 is not working | Software | No | N/A | Fault rectified no SR created | N/A | 2023-06-28 | 11:28 | 2023-06-28 | 12:00 |  | 207
FR-TR-RD-079 | CWS | 4C1CWS | Pumps not running on VFD | NO DEFECTS_26 | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 60 | Not working due to lost of Communication | Software | No | N/A | Trane Supplier rectfied | N/A | 2023-06-15 | 12:00 | 2023-06-15 | 13:00
FR-TR-RD-080 | CWS | 4C1CWS | Pumps not running on VFD | NO DEFECTS_26 | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 60 | Not working due to lost of Communication | Software | No | N/A | Trane Supplier rectfied | N/A | 2023-06-15 | 12:00 | 2023-06-15 | 13:00
FR-TR-RD-081 | CWS | 4C1CWS | Pumps not running on VFD | NO DEFECTS_26 | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 60 | Not working due to lost of Communication | Software | No | N/A | Trane Supplier rectfied | N/A | 2023-06-15 | 12:00 | 2023-06-15 | 13:00
FR-TR-RD-083 | ES | 4C1ES | No running | NO DEFECTS_28 | 2023-06-17 | 10:00 | Alarm idicated from SCADA/BMS System | 60 | Due to commuication | Software | No | N/A | Informed supplier to Check | N/A | 2023-06-19 | 9:00 | 2023-06-19 | 10:00
FR-TR-RD-088 | ES | 4C1ES | No running | NO DEFECTS_28 | 2023-07-01 | 7:00 | Alarm idicated from SCADA/BMS System | 60 | Due to commuication | Software | No | N/A | Informed supplier to Check | N/A | 2023-07-02 | 9:00 | 2023-07-02 | 10:00
FR-TR-RD-089 | ES | 4C1ES | No running | NO DEFECTS_28 | 2023-07-02 | 7:00 | Alarm idicated from SCADA/BMS System | 60 | Due to commuication | Software | No | N/A | Informed supplier to Check | N/A | 2023-07-02 | 9:00 | 2023-07-02 | 10:00
FR-TR-RD-091 | ES | 4C1ES | No running | NO DEFECTS_28 | 2023-06-10 | 10:00 | Alarm idicated from SCADA/BMS System | 60 | Due to commuication | Software | No | N/A | Informed supplier to Check | N/A | 2023-06-11 | 9:00 | 2023-06-11 | 10:00
FR-TR-RD-020 | ACID | 4E1ACID | Door Is Offline | NO DEFECTS_9 | 2023-06-01 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 120 | Door is closed but appear as open in ACID, Controller damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-06-21 | 9:00 | 2023-06-21 | 11:00
FR-TR-RD-031 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-032 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-033 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-034 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-035 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-036 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-037 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-038 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-039 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-040 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-041 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
FR-TR-RD-073 | CHILLER | 4D1CHILLER | Not working in auto Mode | NO DEFETCS_4 | 2023-06-03 | 8:00 | Physical inspection lead to the failure identification | 120 | Programming Issue | Software | No | N/A | Raised PR for Supplier | N/A | 2023-06-20 | 11:00 | 2023-06-20 | 13:00
FR-TR-RD-074 | ACID | 4D1ACID | Not getting open by access card | ACID Card reader issue | 2023-06-23 | 7:00 | Physical inspection lead to the failure identification | 120 | Programming Issue | Software | No | N/A | Informed to ICT team | N/A | 2023-06-26 | 8:00 | 2023-06-26 | 10:00 |  | 200
TR-FRCS-2023-0047 | UPS | 4E1UPS | UPS Failure and Comms loss 13:53 4E1 UPS Failure, loss comm at 4E1, L4 ESZ 4,5,6 switched off, Global Hold applied. Informed EFC and DM. Trains stuck in between 4D1 to 4G1. TS404, TS423, TS421 (in track 01) - TS419, TS409 (track 02) 13:58 ASP 27 activated. 14:09 ASP 27 deactivated due to TS625 stuck before 4C2 PF01 and TS 406 full stopped at 4C2 PF01 14:10 ASP 24 activated from 6D2 to 6H2 14:18 TS 404 loss com, EVACZ activated at L4 ESZ 3 and L6 ESZ1, Request for switch ON, EVACZ normalized 14: 24 ESZ 3, 4,5,6 bypassed, Confirmed switched ON by EFC 14:24 L6 ESZ 1 switched ON14:40 SLV reset all SDD at 4E1 SDD 02 which is occupied by TS 419 and SDD 11 4E1 which is occupied by TS423 14:41 SDD's at 4E1 now blinking in gray, TC normalized SDD's 14:46 TS406 authorized to move in ATC RMF from 4C2 PF01 towards TS404 (loss comm, buffer has been created) before 4D1 PF01 14:50 SDD 08, 101,102 still blinking unable to normalized 14:52 SDD 08, 101,102 now normalized 15:00 TS 419, TS423 and TS 409 started move automatically 15:02 TS 415 started move automatically 15:15 TS421 started move automatically to 4G1 PF01 15:35 T404 wakeup manually due to loss comm, once wakeup authorized the TA onboard to move in ATC-RMF from 4D1 SDD_01_4D1 to 4E1 pocket track,@ 16:05 T404 moved to depot15:56 EVAC1_4C2,EVAC2_4C2,EVAC3_4C2,EVAC4_4C2 and EVAC1_4D1 activated 15:58 L4 ESZ 3, 4,5,6 bypass normalized, Confirmed by EFC16:06 Automatic without timetable(Nominal services) activated | NO DEFETCS_6 | 2023-06-26 | 13:53 | Physical inspection lead to failure identification | 133 | Deactivated due to TS625 stuck before 4C2 PF01 and TS 406 full stopped at 4C2 PF01 | Software | No | N/A | ESZ 3, 4,5,6 bypassed, Confirmed switched ON by EFC14. | N/A | 2023-06-26 | 13:53 | 2023-06-26 | 16:06
FR-TR-RD-044 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-23 | 6:20 | Found alarm in Scada, lead to inspection of failure identification | 180 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-058 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-059 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-060 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-061 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-062 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-063 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-064 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-065 | ACID | 4E1ACID | Door Is Offline | ACID Configuration | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 180 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-08 | 8:00 | 2023-07-08 | 11:00 |  | 201
FR-TR-RD-023 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 240 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-029 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-051 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-052 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-053 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-054 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-055 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-056 | BMS | 4E1BMS | NAE is offline | NO DEFECTS_22 | 2023-06-26 | 8:00 | Physical inspection lead to failure identification | 240 | Programming Issue | Software | No | N/A | Informed BMS team to rectify | N/A | 2023-07-04 | 10:00 | 2023-07-04 | 14:00
FR-TR-RD-057 | BMS | 4E1BMS | NAE is offline | NO DEFECTS_22 | 2023-06-26 | 8:00 | Physical inspection lead to failure identification | 240 | Programming Issue | Software | No | N/A | Informed BMS team to rectify | N/A | 2023-07-04 | 10:00 | 2023-07-04 | 14:00
FR-TR-RD-066 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-067 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-068 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-069 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-070 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-071 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 240 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify | N/A | 2023-07-10 | 9:00 | 2023-07-10 | 13:00
FR-TR-RD-075 | LCS | 4D1LCS | LCP panel relay status appear as off | NO DEFECTS_36 | 2023-06-24 | 15:03 | Found alarm in Scada, lead to the failure identification | 240 | Programming Issue | Software | No | N/A | Informed to BMS team | N/A | 2023-07-03 | 13:00 | 2023-07-03 | 17:00
FR-TR-RD-076 | LCS | 4D1LCS | LCP panel relay status appear as off | NO DEFECTS_36 | 2023-06-24 | 15:03 | Found alarm in Scada, lead to the failure identification | 240 | Programming Issue | Software | No | N/A | Informed to BMS team | N/A | 2023-07-03 | 13:00 | 2023-07-03 | 17:00
FR-TR-RD-077 | LCS | 4D1LCS | LCP panel relay status appear as off | NO DEFECTS_36 | 2023-06-24 | 15:03 | Found alarm in Scada, lead to the failure identification | 240 | Programming Issue | Software | No | N/A | Informed to BMS team | N/A | 2023-07-03 | 13:00 | 2023-07-03 | 17:00
FR-TR-RD-244 | FS | 6E1FS | Leak found and in day fuel tank supply line gasket damage | NO DEFECTS_32 | 24-05-2023 | 12:30 | Caretaking team found the minor leak | 240 | Replaced damaged gasket | harware | No | N/A | Leak found by caretaking team while monitoring system and reyalize in day fuel tank supply line gasket damage then Replaced damaged gasket | N/A | 24-07-2023 | 12:30 | 24-05-2023 | 16:30
FR-TR-RD-093 | ACID | 4G1ACID | Always open, appears intrusion | ACID Configuration | 2023-06-06 | 16:00 | Found alarm in Scada, lead to inspection of failure identification | 270 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-06-18 | 7:00 | 2023-06-18 | 11:30 |  | 201
FR-TR-RD-095 | ACID | 4G1ACID | DOOR IS OFFLINE | ACID Configuration | 2023-12-06 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 270 | Door is closed but appear as open in ACID | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-06-18 | 7:00 | 2023-06-18 | 11:30 |  | 201
FR-TR-RD-022 | CCTV | 4E1CCTV | Configuration Issue | ICT Programming Issue | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-08 | 9:00 | 2023-06-08 | 14:00 |  | 208
FR-TR-RD-024 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
FR-TR-RD-025 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
FR-TR-RD-026 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
FR-TR-RD-027 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
FR-TR-RD-028 | CCTV | 4E1CCTV | Camera is Offline | NO DEFECTS_3 | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
FR-TR-RD-030 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-042 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-043 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-045 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-046 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-047 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-048 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-049 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-050 | INTERCOM | 4E1INTERCOM | Intercom is Offline | NO DEFECTS_35 | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify | N/A | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
FR-TR-RD-072 | CCTV | 4E1CCTV | cameras are offline, Working with IP address, but have issue with ISM | NO DEFECTS_3 | 2023-06-01 | 8:00 | Found in ISM, lead to the failure identification | 300 | Appears offline in ISM | Software | No | N/A | Informed to ICT team | N/A | 2023-06-22 | 9:00 | 2023-06-22 | 14:00
FR-TR-RD-021 | ACID | 4E1ACID | Door is closed at site, still appear as open in system | NO DEFECTS_9 | 2023-06-02 | 8:00 | Found alarm in ACID, lead to inspection of failure identification | 420 | Door alignment problem | Hardware | No | N/A | Raised PR for maintenance | N/A | 2023-06-22 | 7:00 | 2023-06-22 | 14:00
FR-TR-RD-251 | AHUS | 6D2AHUS | AHU's air filter damaged | NO DEFECTS_1 | 28-07-2023 | 11:20 | Caretaking team found | 420 | caretaking team start corrective maintence | harware | no | N/A | AHU's filter damaged due to overdue (Prolong used) And new filter replaced | N/A | 28-07-2023 | 11:20 | 28-07-2023 | 18:20
FR-TR-RD-094 | FCU | 4G1FCU | FCU- inside motor damage | FCU Motor | 2023-12-06 | 7:00 | Found during physical inspection | 450 | Required to confirm by supplier | Hardware | NO | N/A | FCU-4G1-CL-03 New motor received and replaced | N/A | 2023-04-07 | 6:30 | 2023-04-07 | 14:00 |  | 204
FR-TR-RD-092 | ACID | 4G1ACID | DOOR IS OFFLINE | ACID Configuration | 2023-06-06 | 16:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Door is closed but appear as open in ACID | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-01-07 | 7:00 | 2023-01-07 | 16:00 |  | 201
FR-TR-RD-096 | ACID | 4G1ACID | DOOR IS OFFLINE | ACID Configuration | 2023-06-14 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-01-07 | 7:00 | 2023-01-07 | 16:00 |  | 201
FR-TR-RD-097 | ACID | 4G1ACID | DOOR IS OFFLINE | ACID Configuration | 2023-06-14 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-01-07 | 7:00 | 2023-01-07 | 16:00 |  | 201
FR-TR-RD-098 | ACID | 4G1ACID | DOOR IS OFFLINE | ACID Configuration | 2023-06-14 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-01-07 | 7:00 | 2023-01-07 | 16:00 |  | 201
FR-TR-RD-099 | ACID | 4G1ACID | Always open, appears intrusion | NO DEFECTS_9 | 2023-06-14 | 10:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
FR-TR-RD-100 | ACID | 4G1ACID | Always open, appears intrusion | NO DEFECTS_9 | 2023-06-14 | 10:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify | N/A | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
FR-TR-RD-101 | ACID | 4G1ACID | Always open, appears intrusion | NO DEFECTS_9 | 2023-06-23 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | NO | N/A | Informed to ICT Team to Rectify | N/A | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
FR-TR-RD-249 | DWS | 6G1DWS | In 6G1 WC is craked | NO DEFECTS_5 | 25-07-2023 | 13:30 | Flow team has find there was damages | 1110 | Flow team coordinate with caretaking team | harware | no | N/A | Flow team was found that there is damage in WC and caretaking team replaced by new TOILET | N/A | 25-07-2023 | 13:00 | 26-07-2023 | 7:30
FR-TR-RD-106 | CPM | 6F1CPM | INC_20230611_001:- CPM system failed tp add Inhibit chiller, gentrally due to overload CPM system used to add inhibit chiller also to compenstate the load | NO DEFECTS_19 | 2023-06-11 | 12:30 | Checking CPM Workstation | 1680 | Reset CPM system to avoid failed to add inhibhit | Hardware | No | N/A | CLOSED / after reset the system normalized | N/A | 2023-06-11 | 12:30 | 2023-06-12 | 16:30
FR-TR-RD-250 | CHILLER | 6G1CHILLER | 6G1 chiller cicuit 1A of chiller giving alarm of high oil temperature & circuit shutdown | NO DEFECTS_4 | 23-07-2023 | 12:00 | alaram found in chiller PLC | 1752 | Oil coolent TRV & temperature sensor of CHU has been DEFECTSed Send request to supplier | harware | no | N/A | Oil coolent TRV & temperature sensor has been replaced by supplier and issue closed | N/A | 30-07-2023 | 13:00 | 31-07-2023 | 18:12
FR-TR-RD-082 | CWS | 4C1CWS | Leakage from PUMP | NO DEFECTS_26 | 2023-06-12 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 3030 | Mechanical seal broken | Hardware | No | N/A | Informed supplier to change the Seal | N/A | 2023-06-15 | 13:30 | 2023-06-17 | 11:00
FR-TR-RD-245 | CPM | 6G1CPM | immersion temperature sensor failure for supply chw pipe 6G1 CPM 02 | NO DEFECTS_19 | 20-05-2023 | 10:30 | Alaram detected in CPM system | 4380 | Faulty TS sensor is replaced with new sensor | harware | No | N/A | alaram detected in CPM system immersion temperature sensor failure for supply chw pipe 6G1 CPM 02 and Faulty TS sensor is replaced with new sensor | N/A | 20-07-2023 | 10:00 | 2023-07-23 | 13:00
FR-TR-RD-246 | GEN | ITPS6.1GEN | Exhaust louver failed to open during operation | NO DEFECTS_17 | 20-05-2023 | 10:30 | Caretaking team found that louver failed to open | 4380 | louver manually opened to avoid any issue during operation of DG | harware | No | N/A | Exhaust louver failed to open during operation and DG exhaust Louver actuator issue and actuator panel rectified by replacing faulty NC element | N/A | 20-07-2023 | 10:00 | 2023-07-23 | 13:00
FR-TR-RD-104 | MDB | 6D2MDB | INC_20230618_001- Main Incomer, ACB charging motor not properly working. | NO DEFECTS_16 | 2023-06-18 | 14:14 | Caertaking team | 48886 | ACB charging motor not properly working. | Hardware | No | N/A | Letter has been sent to Supplier | N/A | 2023-06-18 | 14:14 | 2023-07-22 | 13:00