## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
TR-INC_L6_20230612_001 | PDP | 6G2PDP | INC_L6_20230612_001:-Pier uplight was damaged accidentally by boom truck while transferring the materials and replaced by new Uplight . |  | 45089 | 0.52083 | Phisically check | 240 | Damage found and driver aggreed that is his mistake | Hardware | No | N/A | Done / New uplight repced by spare materials |  | 45089 | 0.52083 | 45089 | 0.6875
TR-INC_L6_20230627_001 | MDB | 6H2MDB | INC_L6_20230627_001:-DG was working once it receive under voltage signal but due malfunction in MDB-6H2-1G / ACB QG 1.1 the C.B was tripped |  | 45104 | 0.43944 | Caertaking team | 17517 | MDB-6H2- 1G / ACB-QG1.1 Tripped | Hardware | No | N/A | Done/settings have been modified to be match with the coordination study. |  | 45104 | 0.43944 | 45116 | 0.60417
TR-INC_L6_20230620_001 | MCC | 6H2MCC | INC_L6_20230620_001:-the undervoltage relay was damged and replace it |  | 45097 | 0.33333 | Caertaking team | 28090 | Undervoltage relay damged | Hardware | No | N/A | Done/defective part replacment by another |  | 45097 | 0.33333 | 45116 | 0.84028
TR- INC_L6_20230704_001 | SEXF | 6E1SEXF | INC_L6_20230704_001:- Return Air MSFD found closed due to fusible link broken and replaced by spare fusible link and issue closed. |  | 45111 | 0.3125 | Caertaking team | 180 | Repaced new fusible link for MSFD | Hardware | No | N/A | DONE |  | 45111 | 0.3125 | 45111 | 0.4375
TR-INC_L6_20230709_001 | CPM | 6G1CPM | INC_L6_20230709_001: Indicated CPM system flow meter has no value and caretaking team found flowmeter has defected due to short circuit, and replaced new flow meter display and the issue solved. |  | 45120 | 0.3125 | CPM | 83820 | Caretaking team found flow meter display defected | Hardware | No | N/A | DONE / New flow meter display has replaced |  | 45059 | 0.3125 | 45117 | 0.52083
TR-INC_L6_20230703_001 | GEN | 6F1GEN | INC_L6_20230703_001: Caretaking team found controller vibration islolator damaged due to prolong used, and replaced new spare islotaors |  | 45110 | 0.4375 | Caertaking team | 270 | caretaking team sence more vibtration and replaced damaged isolator | Hardware | No | N/A | Done / Vibration isolator has replaced from spare |  | 45110 | 0.4375 | 45110 | 0.625
TR-INC_L6_20230703_002 | TFDS | 6H2TFDS | INC_L6_20230703_002:- Motorized damper pcb board burn due to inner short circuit and it has been replaced new by SAFID supplier |  | 45110 | 0.60417 | TMCS | 1410 | caretaking team isolate the power and keep TMCS in manual to stop stimulation and damper open manually to avoid operation failuer | Hardware | No | N/A | done / new PCB board replaced new by SAFID |  | 45110 | 0.60417 | 45111 | 0.58333