## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
TR-L4-4C1-00001 | ACID | 4C1ACID | Not opening with Card |  | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 0 | No communication | Software | No | N/A | Informed to ICT team to rectify |  | 2023-06-01 | 8:40
TR-L4-4C1-00002 | ACID | 4C1ACID | working with card but not opening frm system |  | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 0 | No communication | Software | No | N/A | Informed to ICT team to rectify |  | 2023-06-01 | 8:40
TR-L4-4C1-00003 | ACID | 4C1ACID | Alarm occuring all the time |  | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 0 | No communication | Software | No | N/A | Informed to ICT team to rectify |  | 2023-06-01 | 8:40
TR-L4-4C1-00004 | ACID | 4C1ACID | Not opening with Card |  | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 0 | No communication | Software | No | N/A | Informed to ICT team to rectify |  | 2023-06-01 | 8:40
TR-L4-4C1-00005 | ACID | 4C1ACID | Not opening with Card |  | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 0 | No communication | Software | No | N/A | Informed to ICT team to rectify |  | 2023-06-01 | 8:40
TR-L4-4C1-00006 | ACID | 4C1ACID | Not opening with Card & system |  | 2023-06-01 | 8:40 | Alarm indicated in Scada/ISM System | 0 | No communication | Software | No | N/A | Informed to ICT team to rectify |  | 2023-06-01 | 8:40
TR-L4-4D1-00003 | ACID | 4D1ACID | Door is always open, not getting lock |  | 2023-06-01 | 7:00 | Found in SCADA Alarms | 0 | Required Configuration | Software | No | N/A | Informed ICT team to rectify acid door |  | 2023-06-01 | 7:00
TR-L4-4D1-00006 | ACID | 4D1ACID | Controller Issue - AC-4D1-CL-028 |  | 2023-06-07 | 9:00 | Found alarm in Scada, lead to the failure identification | 0 | Programming Issue | Software | No | N/A | Informed to ICT team |  | 2023-06-07 | 9:00
TR-L4-4E1-00001 | ACID | 4E1ACID | Door Is Offline - AC-4E1-CL-08 - AC-4E1-CL-29 |  | 2023-06-01 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | Door is closed but appear as open in ACID | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-01 | 9:00
TR-L4-4E1-00003 | ACID | 4E1ACID | Door is closed at site, still appear as open in system - AC-4E1-CL-025 |  | 2023-06-02 | 8:00 | Found alarm in ACID, lead to inspection of failure identification | 0 | Control Board damaged | Hardware | No | N/A | Raised PR for maintenance |  | 2023-06-02 | 8:00
TR-L4-4E1-00004 | ACID | 4E1ACID | Always open, appears intrusion |  | 2023-06-02 | 8:00 | Found alarm in ACID, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-02 | 8:00
TR-L4-4G1-00003 | ACID | 4G1ACID | DOOR IS OFFLINE AC-4G1-TL-01 AC-4G1-GL-101 AC-4G1-PL-02 AC-4G1-GL-05 AC-4G1-GL-100 |  | 2023-06-06 | 16:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | Door is closed but appear as open in ACID | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-06 | 16:00
TR-L4-4G1-00004 | ACID | 4G1ACID | Always open, appears intrusion |  | 2023-06-06 | 17:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-06 | 17:00
TR-L4-4G1-00007 | ACID | 4G1ACID | Configuration Issue |  | 2023-06-06 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-06 | 9:00
TR-L4-4G1-00008 | ACID | 4G1ACID | Always open, appears intrusion |  | 2023-06-06 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | Door is closed but appear as open in ACID | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-06 | 9:00
TR-INC_20230501_001 | ACID | 4A1ACID | ACID • 15:44 ACID_01_6A1 activated leading to traction cut off. Normalized when it has been confirm it was not caused by an intrusion. • 16:46 ACID_01_6A1 activated leading to traction cut off. Normalized when it has been confirm it was not caused by an intrusion. • 16:50 ACID_01_6A1 A Sentinel has been placed in front of the door, then the TC has inhibited the affected sensor from OCC. • 17:53 ACID_01_6A1 activated, with no impact as inhibition was in place. The SIL2 sensor controller has been rectified during the night. |  | 2023-05-01 | 8:00 | SIL2 sensor activated | 129 | SIL2 sensor activated | Software | No | DJV-IHA-REQ-202 | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-01 | 15:44 | 2023-05-01 | 17:53
TR-INC_20230502_001 | ACID | 4A1ACID | ACID 15:44 10 :27 ACID_01_6A1 triggered 2 consecutive times. Inhibited each time. |  | 2023-05-02 | 8:00 | Alarm indicated in Scada/ACID System | 69 | Alarm indicated in Scada/ACID System | Software | No | N/A | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-02 | 16:44 | 2023-05-02 | 17:53
TR-INC_20230504_001 | ACID | 4A1ACID | ACID : 04:59, 07:08 & 07:20 - ACID_01_6A1 triggered 3 times. Inhibition was active hence no traction cutoff. No impact on SA due to mitigation measures. |  | 2023-05-04 | 8:00 | Alarm indicated in Scada/ACID System | 141 | Alarm indicated in Scada/ACID System | Software | No | DJV-IHA-REQ-202 | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-04 | 4:59 | 2023-05-04 | 7:20
TR-INC_20230505_001 | ACID | 4A1ACID | ACID_01_6A1 isolated from SER and inhibited from ATS. Sentinel placed. |  | 2023-05-05 | 8:00 | Alarm indicated in Scada/ACID System | 151 | Alarm indicated in Scada/ACID System | Software | No | N/A | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-05 | 4:59 | 2023-05-05 | 7:30
TR-INC_20230506_001 | ACID | 4A1ACID | ACID_01_6A1 isolated from SER and inhibited from ATS. Sentinel placed. |  | 2023-05-06 | 8:00 | Alarm indicated in Scada/ACID System | 190.1667 | Alarm indicated in Scada/ACID System | Software | No | N/A | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-06 | 5:00 | 2023-05-06 | 8:10
TR-INC_20230507_001 | ACID | 4A1ACID | ACID_01_6A1 isolated from SER and inhibited from ATS. Sentinel placed. |  | 2023-05-07 | 8:00 | Alarm indicated in Scada/ACID System | 152 | Alarm indicated in Scada/ACID System | Software | No | N/A | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-07 | 5:00 | 2023-05-07 | 7:32
TR-INC_20230508_001 | ACID | 4A1ACID | ACID_01_6A1 isolated from SER and inhibited from ATS. Sentinel placed. |  | 2023-05-08 | 8:00 | Alarm indicated in Scada/ACID System | 152 | Alarm indicated in Scada/ACID System | Software | No | N/A | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-08 | 5:00 | 2023-05-08 | 7:32
TR-INC_20230514_001 | ACID | 4A1ACID | ACID_01_6A1 isolated from SER and inhibited from ATS. Sentinel placed |  | 2023-05-14 | 8:00 | Alarm indicated in Scada/ACID System | 131 | Alarm indicated in Scada/ACID System | Software | No | N/A | T connector in SIL door terminaton box replaced which was damaged, |  | 2023-05-14 | 6:00 | 2023-05-14 | 8:11
TR-L4-4G1-00001 | AHUS | 4G1AHUS | UNUSUAL NOISE FROM AHU SUPPLY BLOWER |  | 2023-02-06 | 8:03 | Found during physical inspection | 0 | Required to confirm by supplier | Hardware | No | N/A | PR RAISED TO SUPPILER |  | 2023-02-06 | 8:03
TR-L4-4G1-00002 | DWS | 4G1DWS | WATER LEAKAGE FROM INSIDE THE PUMP INTERNAL SEAL ISSUE |  | 2023-03-06 | 10:00 | Found during physical inspection | 0 | Required to confirm by supplier | Hardware | No | N/A | PR RAISED TO SUPPILER |  | 2023-03-06 | 10:00
TR-L4-4B1-00013 | CBS | 4B1CBS | SOU Module NO:1 damaged |  | 2023-06-08 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair |  | 2023-06-08 | 8:00
TR-L4-4B1-00014 | CBS | 4B1CBS | SOU Module NO:8 damaged |  | 2023-06-08 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair |  | 2023-06-08 | 8:00
TR-L4-4B1-00015 | CBS | 4B1CBS | SOU Module No:2 damaged |  | 2023-06-08 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair |  | 2023-06-08 | 9:00
TR-L4-4B1-00016 | CBS | 4B1CBS | SOU Module NO:4 damaged |  | 2023-06-08 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | due to Overload on Module | Hardware | No | N/A | PR raise and waiting for supplier to repair |  | 2023-06-08 | 9:00
TR-L4-4E1-00002 | CCTV | 4E1CCTV | image not clear |  | 2023-06-01 | 7:00 | Physical inspection lead to failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-01 | 7:00
TR-L4-4E1-00005 | CCTV | 4E1CCTV | Configuration Issue |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
TR-L4-4E1-00006 | CCTV | 4E1CCTV | Cameras are Offline - CMIN-4E1-GL-109 - CMIN-4E1-PL-003 - CFIX-4E1-CL-017 - CFIX-4E1-CL-110 - CMIN-4E1-CL-011 - CMIP-4E1-CL-012 |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-03 | 7:00
TR-L4-4G1-00005 | CCTV | 4E1CCTV | Configuration Issue |  | 2023-06-06 | 16:00 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | NO | N/A | Informed ICT team to rectify |  | 2023-06-06 | 16:00
TR-L4-4B1-00008 | CCTV | 4B1CCTV | Camers Nor workinn L4B1-CMIN-CL-007 L4B1-CMIN-CL-019 L4B1-CMIN-CL-121 L4B1-CMIP-CL-001 L4B1-CMIN-BLU-002 L4B1-CFIX-CL010 L4B1-CFIX-CL101 |  | 2023-06-02 | 9:00 | Monitoring from SCADA/ISM System | 0 | Not Working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration og CCTV |  | 2023-06-02 | 9:00
TR-L4-4C1-00007 | CCTV | 4C1CCTV | No configuration |  | 2023-06-01 | 7:23 | Alarm indicated in Scada/ISM System | 0 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV |  | 2023-06-01 | 7:23
TR-L4-4C1-00008 | CCTV | 4C1CCTV | Camers Nor working CMIN-BL-101 CMIN-GL-003 CMIN-GL-015 CMIN-GL-105 CMIN-GL-105 CMIN-GL-108 CFIX-CL-101 |  | 2023-06-01 | 7:23 | Alarm indicated in Scada/ISM System | 0 | Not working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV |  | 2023-06-01 | 7:23
TR-L4-4D1-00001 | CCTV | 4D1CCTV | cameras are offline, Working with IP address, but have issue with ISM CFIX-CL-110, CMIN-CL-012 |  | 2023-06-01 | 8:00 | Found in ISM, lead to the failure identification | 0 | Appears offline in ISM | Software | No | N/A | Informed to ICT team |  | 2023-06-01 | 8:00
TR-L4-4C1-00012 | CPM | 4C1CPM | Leakage from PUMP |  | 2023-06-12 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Mechanical seal broken | Hardware | No | N/A | Informed supplier to change the Seal |  | 2023-06-12 | 8:00
TR-L4-4C1-00011 | MCC | 4C1MCC | Pumps not running on VFD CHWP-4C1-CL-002 CHWP-4C1-CL-003 CHWP-4C1-CL-004 CHWP-4C1-CL-005 CHWP-4C1-CL-006 |  | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Not working due to lost of Communication | Software | No | N/A | informed electrical team to check |  | 2023-06-06 | 7:23
TR-L4-4D1-00005 | EWH | 4D1EWH | Water Leakage from the Heater |  | 2023-06-04 | 14:00 | Physical inspection lead to the failure identification | 0 | heater have internal leakage | Hardware | No | N/A | Raised PR for Supplier |  | 2023-06-04 | 14:00
TR-L4-4B1-00001 | FCU | 4B1FCU | PCB not working (red color) |  | 2023-06-01 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | PBC not working due to fuse | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 2023-06-01 | 8:00
TR-L4-4B1-00002 | FCU | 4B1FCU | Tranformer burned |  | 2023-06-01 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | due to wrong termination | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 2023-06-01 | 9:00
TR-L4-4B1-00003 | FCU | 4B1FCU | PCB not working & ON/OFF swicth not working |  | 2023-06-01 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | FCU selector swicth not working due to wrong wiring | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 2023-06-01 | 9:00
TR-L4-4B1-00004 | FCU | 4B1FCU | FCU coil Leakage |  | 2023-06-01 | 9:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | water leaking from coil | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 2023-06-01 | 9:00
TR-L4-4B1-00005 | FCU | 4B1FCU | PCB not working (red & Green color) |  | 2023-06-01 | 11:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | PBC not working due to fuse damage | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 2023-06-01 | 11:00
TR-L4-4B1-00006 | FCU | 4B1FCU | PCB not working (red color) |  | 2023-06-01 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | PBC not working due to fuse | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 2023-06-01 | 8:00
TR-L4-4B1-00007 | FCU | 4B1FCU | FCU Motor winding got damaged due to wrong termination |  | 2023-06-01 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | Due to overload on motor | Hardware | No | N/A | PR raise and waiting for supplier to repair |  | 2023-06-01 | 8:00
TR-L4-4C1-00009 | FCU | 4C1FCU | Motor damaged |  | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Due to running | Hardware | No | N/A | Informed supplier to change the Motor |  | 2023-06-02 | 8:00
TR-L4-4C1-000010 | FCU | 4C1FCU | Blower damaged |  | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Due to running | Hardware | No | N/A | Informed supplier to change the Blower |  | 2023-06-02 | 8:00
TR-L4-4C1-000011 | FCU | 4C1FCU | Motor Not running on AUTO |  | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Motor start problem | Hardware | No | N/A | informed supplier to check |  | 2023-06-02 | 8:00
TR-L4-4D1-00002 | FCU | 4D1FCU | Blower motor damaged |  | 2023-06-01 | 10:00 | Physical inspection lead to the failure identification | 0 | Required to replace motor | Hardware | No | N/A | Raised PR for spare part |  | 2023-06-01 | 10:00
TR-L4-4D1-00007 | FCU | 4D1FCU | Controller damged - FCU-4D1-GL-004A |  | 2023-06-10 | 11:00 | Physical inspection lead to the failure identification | 0 | Required to replace PCB & controller | Hardware | No | N/A | Raised PR for spare part |  | 2023-06-10 | 11:00
TR-L4-4E1-00008 | FCU | 4E1FCU | Not working |  | 2023-06-08 | 11:00 | Found alarm in BMS, lead to inspection of failure identification | 0 | Control Board damaged | Hardware | No | N/A | Raised PR for maintenance |  | 2023-06-08 | 11:00
TR-L4-4G1-00006 | FCU | 4G1FCU | FCU- inside motor damage |  | 2023-06-06 | 7:00 | Found during physical inspection | 0 | Required to confirm by supplier | Hardware | NO | N/A | Sent to suppiler |  | 2023-06-06 | 7:00
TR-L4-4B1-00020 | FCU | 4B1FCU | Graphics not shown |  | 2023-06-13 | 7:00 | Alarm idicated from SCADA/BMS System | 0 | FCU working fine but BMS system Graphics not shown | Software | No | N/A | Informed BMS team to rectify |  | 2023-06-13 | 7:00
TR-L4-4B1-00017 | FDS | 4B1FDS | Maintenace alart for Dirty |  | 2023-06-11 | 6:00 | Alarm idicated from Fire Alarm System | 0 | Due to dust accumlated on Smoke Detector | Hardware | No | N/A | ELECTRICAL TEAM |  | 2023-06-11 | 6:00
TR-L4-4B1-00018 | FDS | 4B1FDS | Maintenace alart for Dirty |  | 2023-06-11 | 9:00 | Alarm idicated from Fire Alarm System | 0 | Due to dust accumlated on Smoke Detector | Hardware | No | N/A | ELECTRICAL TEAM |  | 2023-06-11 | 9:00
TR-L4-4B1-00012 | LCS | 4B1LCS | Controller Module No:2 damaged |  | 2023-06-07 | 11:00 | Alarm idicated from SCADA/BMS System | 0 | due to Overload on Controller Module | Hardware | No | N/A | Informed BMS team to the will rectify |  | 2023-06-07 | 11:00
TR-L4-4E1-00007 | LCS | 4E1LCS | Lights are not turning ON & OFF as per schedule |  | 2023-06-04 | 5:00 | Physical inspection lead to failure identification | 0 | Programming Issue | Software | No | N/A | Informed to BMS team to rectify |  | 2023-06-04 | 5:00
TR-L4-4B1-00010 | MCC | 4B1MCC | contartor got damaged |  | 2023-06-05 | 10:00 | Alarm idicated from SCADA/BMS System | 0 | due to wrong termination | Hardware | No | N/A | need to Informed splier for cotactor |  | 2023-06-05 | 10:00
TR-L4-4B1-00011 | MCC | 4B1MCC | contartor got damaged |  | 2023-06-05 | 10:00 | Alarm idicated from SCADA/BMS System | 0 | due to wrong termination | Hardware | No | N/A | need to Informed splier for cotactor |  | 2023-06-05 | 10:00
TR-L4-4C1-00013 | MCC | 4C1MCC | contartor got damaged |  | 2023-06-12 | 10:00 | Alarm idicated from SCADA/BMS System | 0 | due to wrong termination | Hardware | No | N/A | Informed supplier to change the Contactor |  | 2023-06-12 | 10:00
TR-L4-4C1-00014 | MCC | 4C1MCC | contartor got damaged |  | 2023-06-12 | 10:00 | Alarm idicated from SCADA/BMS System | 0 | due to wrong termination | Hardware | No | N/A | Informed supplier to change the Contactor |  | 2023-06-12 | 10:00
TR-L4-4B1-00019 | MCC | 4B1MCC | Contactor not working |  | 2023-06-12 | 8:00 | Alarm idicated from SCADA/BMS System | 0 | MCC Contactor not give the Volt, due to L3 power failure. | Hardware | No | N/A | need to Inform Meta team |  | 2023-06-12 | 8:00
TR-L4-4D1-00004 | CWS | 4D1CWS | Not working in auto Mode |  | 2023-06-03 | 8:00 | Physical inspection lead to the failure identification | 0 | Programming Issue | Software | No | N/A | Raised PR for Supplier |  | 2023-06-03 | 8:00
TR-L4-4B1-00009 | SEXF | 4B1SEXF | SEF Motor winding got damaged |  | 2023-06-04 | 8:00 | Alarm idicated from SCADA/BMS System | 0 | Due to MCC Contactor not give the Volt, due to L3 power failure. | Hardware | No | N/A | Sent motor to workshop for rewinding |  | 2023-06-04 | 8:00
TR-L4-4C1-00010 | SEXF | 4C1SEXF | Fan gets trippped |  | 2023-06-04 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Due to Over load | Hardware | No | N/A | informed electrical team to check |  | 2023-06-04 | 8:00
TR-INC_20230503_001 | UPS | 4C1UPS | UPS Around 5:50am the 4C1 UPS has been manually switched off for an unknown reason (investigation on-going) The UPS has been switch-on back at around 06:13. |  | 2023-05-03 | 8:00 | Physical Inspection | 23 | Physical Inspection | Hardware | No | N/A | 6C1 UPS shutdown Incident M3-CJV-RPT-HSEFD-ELS-000001 rev. AA (transmittal to RAMPED M3-FST-TRANSMIT-139888) |  | 2023-05-03 | 5:50 | 2023-05-03 | 6:13
TR-INC_20230508_002 | TMCS | 6H2TMCS | 06:05: Train 611 in STL_16_6H2 had IOS40 “HVAC unit cooling fault with interior temperature” alarm |  | 2023-05-08 | 8:00 | Alarm indication | 188 | Alarm indication | Hardware | No | N/A | Linked to 6H2 abnormal tunnel temperature |  | 2023-05-08 | 6:05 | 2023-05-08 | 9:13
TR-INC_20230508_003 | TMCS | 6H2TMCS | 06:23 – Alarm L6H2_LHDP01 Linear Heat Detection temperature above 51 C |  | 2023-05-08 | 8:00 | Alarm indication | 138 | Alarm indication | Hardware | No | N/A | Pending |  | 2023-05-08 | 6:23 | 2023-05-08 | 8:41
TR-INC_20230513_002 | TMCS | 6H2TMCS | [INC-20230513-003] L6 QCTT: 13 trips impacted; 615 with one Airco Unit Fault + IOS39 mainly triggered in 6A1 when train doors are opened. To check if OTE and 6A1 Platforms AirCo are working fine. |  | 2023-05-13 | 8:00 | Alarm indicated in Scada/ACID System | 136 | Alarm indicated in Scada/ACID System | Hardware | No | N/A | TSY: High Pressure fault has been triggreded in 6H2 stabling position due to abnormal tunel temperature during the pre-cooling phase of the train. With High Pressure fault only 2 compressors out of 4 can work at the sametime.TS615 was then running with reiduced cooling capacity. more the IOS39 was trigged each time train stopped and open doors in 6H2 and 6A1 station where plateforms are not cooled (without airco). High Pressure fault was cleared and Airco back to normal after train restart. INC-20230513-003 Normal behavior due to site conditions. To be closed. |  | 2023-05-13 | 6:00 | 2023-05-13 | 8:16
TR-INC_20230514_003 | TMCS | 6H2TMCS | Activation of the water mist system to cool the stabling position in 6H2 |  | 2023-05-14 | 8:00 | Alarm indication | 133 | Alarm indication | Hardware | No | FMECA-WMS-008 | Pending |  | 2023-05-14 | 6:00 | 2023-05-14 | 8:13
TR-INC_20230516_002 | TMCS | 6H2TMCS | [INC_20230516_002] L6 QCTT: 3 trips were impacted (with QCTT = 0.9 / IOS39). The 3 Trains (TS623, TS612 & TS613) moved out from 6H2 stabling for morning peak injection. |  | 2023-05-16 | 8:00 | Alarm indication | 156 | Alarm indication | Hardware | No | N/A | Pending |  | 2023-05-16 | 6:00 | 2023-05-16 | 8:36
TR-INC_20230517_002 | TMCS | 6H2TMCS | L6 QCTT: Minor impact. 3 trips with QCTT = 0.9 / IOS39; Both impacted trains TS617 & TS610 were moved out from 6H2 stabling for morning peak injection. Linked to TVS management in 6H2. |  | 2023-05-17 | 8:00 | Alarm indication | 226 | Alarm indication | Hardware | No | PHA_CJV_312 | Pending |  | 2023-05-17 | 6:00 | 2023-05-17 | 9:46
TR-INC_20230518_002 | TMCS | 6H2TMCS | L6 QCTT: 2 trips with QCTT = 0.9 / IOS39; Both trains TS602 & TS616 were moved out from 6H2 stabling for morning peak injection. TVS management in 6H2 under clarification. |  | 2023-05-18 | 8:00 | Alarm indication | 273 | Alarm indication | Hardware | No | PHA_CJV_312 | Pending |  | 2023-05-18 | 6:00 | 2023-05-18 | 10:33
TR-INC_20230519_002 | TMCS | 6H2TMCS | L6 QCTT: 1 trip with QCTT = 0.9 / IOS39; Trains TS610 were moved out from 6H2 stabling for morning peak injection. TVS management in 6H2 under clarification. |  | 2023-05-19 | 8:00 | Alarm indication | 382 | Alarm indication | Hardware | No | PHA_CJV_312 | Pending |  | 2023-05-19 | 6:00 | 2023-05-19 | 12:22