## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
TR-FRCS-2023-0006 | UPS | 6H2UPS | At 10:37hrs:• EFC remotely switch OFF the CB1 of PP6D1 using SCADA WS.This is part of the test case, EFC opens incomer CB1 by SCADA• Normally Open (NO) CBs in TPS and LPS loop auto reclosed.Part of test case – NO CBs are working as per design• P&R 6.4 LPS CB2 and PP6H2 CB4 tripped with 86 lockout alarm. Not part of the test case – should not supposed to happen) FAST to investigate the root cause.• Affected LPS are 6D2, 6E1, 6F1, P&R 6.2, 6G1, 6G2, 6H1, 6H2, and P&R 6.4. All generator started, however charging of UPS in 6H2 not working – see attached video.• COGS of ITPS 6.1, 6D2, and 6F1 tripped with 86 lockout alarm while 6E1 TPS tripped due to undervoltage.No affect to train movement as Normally Open (NO) CBs in TPS 6F1 (CB2) and TPS 6G1 (CB1) auto-reclosed successfully At 11:53hrs EFC closed PP6D1 CB1 upon the instruction by FAST and approve by Test Case Manager because UPS battery in 6H2 almost drained. Finally, test case was completed, however, 2 undesired failures (UPS failure and CB tripping in P&RP6.4 (CB2) and 6H2 (CB4)) occurred which are not part of the exercise FAST must investigate. | Power Malfunction/Internal damage | UPS-Power damage | 14-062023 | 10:37:00 | • P&R 6.4 LPS CB2 and PP6H2 CB4 tripped with 86 lockout alarm. Not part of the test case – should not supposed to happen) FAST to investigate the root cause.• Affected LPS are 6D2, 6E1, 6F1, P&R 6.2, 6G1, 6G2, 6H1, 6H2, and P&R 6.4. All generator started, however charging of UPS in 6H2 not working• COGS of ITPS 6.1, 6D2, and 6F1 tripped with 86 lockout alarm while 6E1 TPS tripped due to undervoltage. | 76 | • P&R 6.4 LPS CB2 and PP6H2 CB4 tripped with 86 lockout alarm. Not part of the test case – should not supposed to happen) FAST to investigate the root cause.• Affected LPS are 6D2, 6E1, 6F1, P&R 6.2, 6G1, 6G2, 6H1, 6H2, and P&R 6.4. All generator started, however charging of UPS in 6H2 not working• COGS of ITPS 6.1, 6D2, and 6F1 tripped with 86 lockout alarm while 6E1 TPS tripped due to undervoltage. | Hardware | Yes | FMECA_CJV092 | EFC closed PP6D1 CB1 upon the instruction by FAST and approve by Test Case Manager because UPS battery in 6H2 almost drained. Finally, test case was completed, however, 2 undesired failures (UPS failure and CB tripping in P&RP6.4 (CB2) and 6H2 (CB4)) occurred which are not part of the exercise FAST must investigate. | 14-06-2023 | 10:37:00 | 14-06-2023 | 11:53:00