## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
TR-L4-4C1-00025 | CHILLER | 4C1CHILLER | Leakage from PUMP |  | 2023-06-12 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 2730 | Mechanical seal broken | Hardware | No | N/A | Informed supplier to change the Seal |  | 2023-06-15 | 13:30 | 2023-06-17 | 11:00
TR-L4-4E1-00049 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 600 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 19:00
TR-L4-4E1-00048 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 540 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 18:00
TR-L4-4G1-00009 | ACID | 4G1ACID | DOOR IS OFFLINE |  | 2023-06-14 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
TR-L4-4G1-00010 | ACID | 4G1ACID | DOOR IS OFFLINE |  | 2023-06-14 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
TR-L4-4G1-00011 | ACID | DOORS | DOOR IS OFFLINE |  | 2023-06-14 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
TR-L4-4G1-00024 | ACID | 4G1ACID | Always open, appears intrusion |  | 2023-06-14 | 10:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
TR-L4-4G1-00025 | ACID | 4G1ACID | Always open, appears intrusion |  | 2023-06-14 | 10:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
TR-L4-4G1-00029 | ACID | 4G1ACID | Always open, appears intrusion |  | 2023-06-23 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 540 | Programming Issue | Software | No | N/A | Informed to ICT Team to Rectify |  | 2023-01-07 | 7:00 | 2023-01-07 | 16:00
TR-L4-4E1-00047 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 480 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 17:00
TR-L4-4E1-00046 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 420 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 16:00
TR-L4-4E1-00045 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 360 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 15:00
TR-L4-4E1-00010 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
TR-L4-4E1-00011 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
TR-L4-4E1-00012 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
TR-L4-4E1-00013 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
TR-L4-4E1-00014 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-08 | 9:00 | 2023-06-08 | 14:00
TR-L4-4E1-00024 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
TR-L4-4E1-00038 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
TR-L4-4E1-00039 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
TR-L4-4E1-00044 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-24 | 8:00 | Physical inspection lead to failure identification | 300 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-07-04 | 9:00 | 2023-07-04 | 14:00
TR-L4-4D1-00019 | LCS | 4D1LCS | LCP panel relay status appear as off |  | 2023-06-24 | 15:03 | Found alarm in Scada, lead to the failure identification | 240 | Programming Issue | Software | No | N/A | Informed to BMS team |  | 2023-07-03 | 13:00 | 2023-07-03 | 17:00
TR-L4-4D1-00020 | LCS | 4D1LCS | LCP panel relay status appear as off |  | 2023-06-24 | 15:03 | Found alarm in Scada, lead to the failure identification | 240 | Programming Issue | Software | No | N/A | Informed to BMS team |  | 2023-07-03 | 13:00 | 2023-07-03 | 17:00
TR-L4-4D1-00021 | LCS | 4D1LCS | LCP panel relay status appear as off |  | 2023-06-24 | 15:03 | Found alarm in Scada, lead to the failure identification | 240 | Programming Issue | Software | No | N/A | Informed to BMS team |  | 2023-07-03 | 13:00 | 2023-07-03 | 17:00
TR-L4-4E1-00055 | BMS | 4E1BMS | NAE is offline |  | 2023-06-26 | 8:00 | Physical inspection lead to failure identification | 240 | Programming Issue | Software | No | N/A | Informed BMS team to rectify |  | 2023-07-04 | 10:00 | 2023-07-04 | 14:00
TR-L4-4E1-00056 | BMS | 4E1BMS | NAE is offline |  | 2023-06-26 | 8:00 | Physical inspection lead to failure identification | 240 | Programming Issue | Software | No | N/A | Informed BMS team to rectify |  | 2023-07-04 | 10:00 | 2023-07-04 | 14:00
TR-L4-4D1-00017 | ACID | 4D1ACID | Not getting open by access card |  | 2023-06-23 | 7:00 | Physical inspection lead to the failure identification | 120 | Programming Issue | Software | No | N/A | Informed to ICT team |  | 2023-06-26 | 8:00 | 2023-06-26 | 10:00
TR-L4-4E1-00025 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00026 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00027 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00028 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00029 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00030 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00031 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00032 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00033 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00035 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4E1-00036 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 120 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-19 | 7:00 | 2023-06-19 | 9:00
TR-L4-4C1-00029 | ES | 4C1ES | No running |  | 2023-06-17 | 10:00 | Alarm idicated from SCADA/BMS System | 60 | Due to commuication | Software | No | N/A | Informed supplier to Check |  | 2023-06-19 | 9:00 | 2023-06-19 | 10:00
TR-L4-4C1-00034 | ES | 4C1ES | No running |  | 2023-07-01 | 7:00 | Alarm idicated from SCADA/BMS System | 60 | Due to commuication | Software | No | N/A | Informed supplier to Check |  | 2023-07-02 | 9:00 | 2023-07-02 | 10:00
TR-L4-4C1-00035 | ES | 4C1ES | No running |  | 2023-07-02 | 7:00 | Alarm idicated from SCADA/BMS System | 60 | Due to commuication | Software | No | N/A | Informed supplier to Check |  | 2023-07-02 | 9:00 | 2023-07-02 | 10:00
TR-L4-4C1-00030 | AHUS | 4C1AHUS | AHU BELT BROKEN |  | 2023-06-20 | 10:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 30 | DUE TO RUNNING | Hardware | No | N/A | Change belt |  | 2023-06-20 | 11:00 | 2023-06-20 | 11:30
TR-L4-4C1-00031 | FDS | 4C1FDS | dirty detector |  | 2023-06-22 | 6:00 | Alarm idicated from SCADA/BMS System | 30 | due to dust | Hardware | No | N/A | clean the detector |  | 2023-06-22 | 11:00 | 2023-06-22 | 11:30
TR-L4-4C1-00032 | FDS | 4C1FDS | dirty detector |  | 2023-06-23 | 6:00 | Alarm idicated from SCADA/BMS System | 30 | due to dust | Hardware | No | N/A | clean the detector |  | 2023-06-23 | 9:00 | 2023-06-23 | 9:30
TR-L4-4C1-00033 | FDS | 4C1FDS | dirty detector |  | 2023-06-25 | 6:00 | Alarm idicated from SCADA/BMS System | 30 | due to dust | Hardware | No | N/A | clean the detector |  | 2023-06-25 | 10:00 | 2023-06-25 | 10:30
TR-L4-4C1-00019 | MCC | 4C1MCC | Pumps not running on VFD |  | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 60 | Not working due to lost of Communication | Software | No | N/A | Trane Supplier rectfied |  | 2023-06-15 | 12:00 | 2023-06-15 | 13:00
TR-L4-4C1-00020 | MCC | 4C1MCC | Pumps not running on VFD |  | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 60 | Not working due to lost of Communication | Software | No | N/A | Trane Supplier rectfied |  | 2023-06-15 | 12:00 | 2023-06-15 | 13:00
TR-L4-4C1-00021 | MCC | 4C1MCC | Pumps not running on VFD |  | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 60 | Not working due to lost of Communication | Software | No | N/A | Trane Supplier rectfied |  | 2023-06-15 | 12:00 | 2023-06-15 | 13:00
TR-INC_L6_20230612_001 | PDP | 6G2PDP | INC_L6_20230612_001:-Pier uplight was damaged accidentally by boom truck while transferring the materials and replaced by new Uplight . |  | 2023-06-12 | 12:30 | Phisically check | 240 | Damage found and driver aggreed that is his mistake | Hardware | No | N/A | Done / New uplight repced by spare materials |  | 2023-06-12 | 12:30 | 2023-06-12 | 16:30
TR-L4-4C1-00015 | FCU | 4C1FCU | Motor damaged |  | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Due to running | Hardware | No | N/A | Informed supplier to change the Motor |  | 2023-06-02 | 8:00
TR-L4-4C1-00016 | FCU | 4C1FCU | Blower damaged |  | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Due to running | Hardware | No | N/A | Informed supplier to change the Blower |  | 2023-06-02 | 8:00
TR-L4-4C1-00017 | FCU | 4C1FCU | Motor Not running on AUTO |  | 2023-06-02 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Motor start problem | Hardware | No | N/A | informed supplier to check |  | 2023-06-02 | 8:00
TR-L4-4E1-00009 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-03 | 7:00
TR-L4-4E1-00015 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-03 | 7:00 | Found alarm in ISM, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-03 | 7:00
TR-L4-4E1-00016 | LCS | 4E1LCS | Lights are not turning ON & OFF as per schedule |  | 2023-06-04 | 5:00 | Physical inspection lead to failure identification | 0 | Programming Issue | Software | No | N/A | Informed to BMS team to rectify |  | 2023-06-04 | 5:00
TR-L4-4C1-00018 | SEXF | 4C1SEXF | Fan gets trippped |  | 2023-06-04 | 8:00 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Due to Over load | Hardware | No | N/A | informed electrical team to check |  | 2023-06-04 | 8:00
TR-L4-4C1-00022 | MCC | 4C1MCC | Pumps not running on VFD |  | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Not working due to lost of Communication | Software | No | N/A | informed electrical team to check |  | 2023-06-06 | 7:23
TR-L4-4C1-00023 | MCC | 4C1MCC | Pumps not running on VFD |  | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Not working due to lost of Communication | Software | No | N/A | informed electrical team to check |  | 2023-06-06 | 7:23
TR-L4-4C1-00024 | MCC | 4C1MCC | Pumps not running on VFD |  | 2023-06-06 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Not working due to lost of Communication | Software | No | N/A | informed electrical team to check |  | 2023-06-06 | 7:23
TR-L4-4D1-00008 | ACID | 4D1ACID | Controller Issue |  | 2023-06-07 | 9:00 | Found alarm in Scada, lead to the failure identification | 0 | Programming Issue | Software | No | N/A | Informed to ICT team |  | 2023-06-07 | 9:00
TR-L4-4E1-00018 | BMS | 4E1BMS | BMS server communication set to failed |  | 2023-06-08 | 19:58 | Found alarm in Scada, lead to inspection of failure identification | 0 | Scada Programming Base line issue | Software | No | N/A |  |  | 2023-06-08 | 19:58
TR-L4-4E1-00019 | FDS | 4E1FDS | FACP PLC communication set to failed |  | 2023-06-08 | 19:58 | Found alarm in Scada, lead to inspection of failure identification | 0 | Scada Programming Base line issue | Software | No | N/A |  |  | 2023-06-08 | 19:58
TR-L4-4E1-00017 | FCU | 4E1FCU | Not working |  | 2023-06-08 | 11:00 | Found alarm in BMS, lead to inspection of failure identification | 0 | Control Board damaged | Hardware | No | N/A | Raised PR for maintenance |  | 2023-06-08 | 11:00
TR-L4-4D1-00009 | FCU | 4D1FCU | Controller & PCB damged |  | 2023-06-10 | 11:00 | Physical inspection lead to the failure identification | 0 | Required to replace PCB & controller | Hardware | No | N/A | Raised PR for spare part |  | 2023-06-10 | 11:00
TR-L4-4D1-00010 | FCU | 4D1FCU | Controller & PCB damged |  | 2023-06-10 | 11:00 | Physical inspection lead to the failure identification | 0 | Required to replace PCB & controller | Hardware | No | N/A | Raised PR for spare part |  | 2023-06-10 | 11:00
TR-L4-4C1-00026 | MCC | 4C1MCC | contartor got damaged |  | 2023-06-12 | 10:00 | Alarm idicated from SCADA/BMS System | 0 | due to wrong termination | Hardware | No | N/A | Informed supplier to change the Contactor |  | 2023-06-12 | 10:00
TR-L4-4C1-00027 | MCC | 4C1MCC | contartor got damaged |  | 2023-06-12 | 10:00 | Alarm idicated from SCADA/BMS System | 0 | due to wrong termination | Hardware | No | N/A | Informed supplier to change the Contactor |  | 2023-06-12 | 10:00
TR-L4-4E1-00020 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-13 | 14:30 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-13 | 14:30
TR-L4-4E1-00021 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-13 | 14:30 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-13 | 14:30
TR-L4-4E1-00022 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-13 | 14:30 | Found alarm in Scada, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-13 | 14:30
TR-L4-4G1-00026 | FCU | 4G1FCU | Remaining to configure in BMS work station |  | 2023-06-14 | 11:00 | Found during physical inspection | 0 | The fcu is installing later that’s why still remaining to programming in BMS Work station by JCI TEAM | Hardware | No | N/A | Informed BMS team to rectify |  | 2023-06-14 | 11:00
TR-L4-4G1-00022 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 10:00 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 10:00
TR-L4-4G1-00023 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 10:00 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 10:00
TR-L4-4G1-00012 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00013 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00014 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00015 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | This camera repeating two times in ISM, and its offline | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00016 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00017 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00018 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00019 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00020 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4G1-00021 | CCTV | 4G1CCTV | Configuration Issue |  | 2023-06-14 | 9:30 | Found alarm in ISM, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 9:30
TR-L4-4E1-00023 | ACID | 4E1ACID | Lock is not getting open by access card |  | 2023-06-14 | 7:00 | Physical inspection lead to failure identification | 0 |  | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-14 | 7:00
TR-L4-4E1-00034 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 0 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-15 | 8:00
TR-L4-4E1-00037 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 0 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-15 | 8:00
TR-L4-4E1-00040 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-15 | 8:00
TR-L4-4E1-00041 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 0 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-15 | 8:00
TR-L4-4E1-00042 | INTERCOM | 4E1INTERCOM | Intercom is Offline |  | 2023-06-15 | 8:00 | Physical inspection lead to failure identification | 0 | ICT Rack Switch damaged | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-15 | 8:00
TR-L4-4C1-00028 | MCC | 4C1MCC | Pumps not running |  | 2023-06-16 | 7:23 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 0 | Not working due to electrical Problem | Hardware | No | N/A | informed electrical team to check |  | 2023-06-16 | 7:23
TR-L4-4D1-00011 | BMS | 4D1BMS | BMS server communication set to failed |  | 2023-06-18 | 8:38 | Found alarm in Scada, lead to inspection of failure identification | 0 | Scada Programming Base line issue | Software | No | N/A |  |  | 2023-06-18 | 8:38
TR-L4-4D1-00012 | FDS | 4D1FDS | FACP PLC communication set to failed |  | 2023-06-18 | 8:38 | Found alarm in Scada, lead to inspection of failure identification | 0 | Scada Programming Base line issue | Software | No | N/A |  |  | 2023-06-18 | 8:38
TR-L4-4G1-00027 | BMS | 4G1BMS | Scada Base line programming issue |  | 2023-06-18 | 8:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | BMS-Server Communication faild- and the error is SCADA Programming Base line issue | Software | No | N/A |  |  | 2023-06-18 | 8:00
TR-L4-4G1-00028 | FDS | 4G1FDS | Scada Base line programming issue |  | 2023-06-18 | 8:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | BMS-Server Communication faild- and the error is SCADA Programming Base line issue | Software | No | N/A |  |  | 2023-06-18 | 8:00
TR-L4-4B1-00021 | CCTV | 4B1CCTV | Not configure |  | 2023-06-18 | 9:00 | Monitoring from SCADA/ISM System | 0 | Not Working due to lost of Communication | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-18 | 9:00
TR-L4-4B1-00022 | CCTV | 4B1CCTV | Offline |  | 2023-06-18 | 9:00 | Monitoring from SCADA/ISM System | 0 | Not Working due to lost of Communication | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-18 | 9:00
TR-L4-4D1-00013 | FS | 4D1FS | Day Tank Fuel Level Sensor not indicating fuel level in EVO panel |  | 2023-06-20 | 13:00 | Physical inspection lead to the failure identification | 0 | Level Sensor communication issue | Software | No | N/A | Informed to supplier |  | 2023-06-20 | 13:00
TR-L4-4D1-00014 | CPM | 4D1CPM | con 2, CPM is not working on VFD mode |  | 2023-06-21 | 16:00 | Physical inspection lead to the failure identification | 0 | CPM programming issue | Software | No | N/A | Informed to supplier |  | 2023-06-21 | 16:00
TR-L4-4B1-00023 | CPM | 4B1CPM | PCB not working (Green color) |  | 2023-06-20 | 11:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | PBC not working due to cable lose connection | Hardware | No | N/A | Electrical team will be rectify |  | 2023-06-20 | 11:00
TR-L4-4B1-00024 | MDB | 4B1MDB | Remote mode not working |  | 2023-06-22 | 8:00 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 0 | BMS cable wrong connection | Hardware | No | N/A | BMS team will be rectify |  | 2023-06-22 | 8:00
TR-L4-4D1-00015 | ACID | 4D1ACID | Not getting open by access card |  | 2023-06-23 | 7:00 | Physical inspection lead to the failure identification | 0 | Programming Issue | Software | No | N/A | Informed to ICT team |  | 2023-06-23 | 7:00
TR-L4-4D1-00016 | ACID | 4D1ACID | Not getting open by access card |  | 2023-06-23 | 7:00 | Physical inspection lead to the failure identification | 0 | Programming Issue | Software | No | N/A | Informed to ICT team |  | 2023-06-23 | 7:00
TR-L4-4E1-00043 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-23 | 6:20 | Found alarm in Scada, lead to inspection of failure identification | 0 | Programming Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-23 | 6:20
TR-L4-4D1-00022 | INTERCOM | 4D1INTERCOM | cameras are offline, Working with IP address, but have issue with ISM |  | 2023-06-24 | 20:52 | Found alarm in Scada, lead to the failure identification | 0 | Appears offline in ISM | Software | No | N/A | Need to rectify from OCC |  | 2023-06-24 | 20:52
TR-L4-4G1-00030 | FPUMP (BUILD) | 4G1FPUMP (BUILD) | WATER LEAKAGE FROM INSIDE THE PUMP INTERNAL SEAL ISSUE |  | 2023-06-24 | 9:00 | Found during physical inspection | 0 | Required to confirm by supplier | Hardware | No | N/A | PR RAISED TO SUPPILER |  | 2023-06-24 | 9:00
TR-L4-4G1-00031 | ES | 4G1ES | General faults |  | 2023-06-24 | 9:00 | Found alarm in Scada, lead to inspection of failure identification | 0 | Suddenly stop with faults error / Required to confirm by supplier | Hardware | No | N/A | Informed to OTIS Team to Rectify |  | 2023-06-24 | 9:00
TR-L4-4E1-00050 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-24 | 8:43
TR-L4-4E1-00051 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-24 | 8:43
TR-L4-4E1-00052 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-24 | 8:43
TR-L4-4E1-00053 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-24 | 8:43
TR-L4-4E1-00054 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-24 | 8:43 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-24 | 8:43
TR-L4-4D1-00018 | BMS | 4D1BMS | BMS graphics not appearing, can't access equipment to check & rectify for any alarm |  | 2023-06-24 | 6:00 | Physical inspection lead to the failure identification | 0 | Programming Issue | Software | No | N/A | Informed to BMS team |  | 2023-06-24 | 6:00
TR-L4-4E1-00057 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00058 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00059 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00060 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00061 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00062 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00063 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00064 | ACID | 4E1ACID | Door Is Offline |  | 2023-06-26 | 14:55 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Network Issue | Software | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:55
TR-L4-4E1-00066 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:53
TR-L4-4E1-00067 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:53
TR-L4-4E1-00068 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:53
TR-L4-4E1-00069 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:53
TR-L4-4E1-00070 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:53
TR-L4-4E1-00071 | CCTV | 4E1CCTV | Camera is Offline |  | 2023-06-26 | 14:53 | Found alarm in Scada, lead to inspection of failure identification | 0 | ICT Rack Switch damaged | Hardware | No | N/A | Informed ICT team to rectify |  | 2023-06-26 | 14:53
TR-L4-4E1-00065 | MDB | 4E1MDB | Power Shutdown |  | 2023-06-26 | 13:30 | Power Failure in station | 0 | PLC is not giving the command to close the MDB outgoing breaker , and the UPS covers the power until the battery is drained | Software | No | N/A | Informed to Generatoe Supplier (Cumins) |  | 2023-06-26 | 13:30
TR-L4-4D1-00023 | ACID | 4D1ACID | Door always appear as open, at site when it's closed also |  | 2023-06-26 | 6:23 | Found alarm in Scada, lead to the failure identification | 0 | Acid Relay damaged | Hardware | No | N/A | Informed to ICT team |  | 2023-06-26 | 6:23
TR-L4-4D1-00024 | ACID | 4D1ACID | Door always appear as open, at site when it's closed also |  | 2023-06-26 | 6:23 | Found alarm in Scada, lead to the failure identification | 0 | Acid Relay damaged | Hardware | No | N/A | Informed to ICT team |  | 2023-06-26 | 6:23
TR-L4-4D1-00025 | INTERCOM | 4D1INTERCOM | cameras are offline, Working with IP address, but have issue with ISM |  | 2023-06-27 | 13:47 | Found alarm in Scada, lead to the failure identification | 0 | Appears offline in ISM | Software | No | N/A | Need to rectify from OCC |  | 2023-06-27 | 13:47
TR-L4-4E1-00072 | FDS | 4E1FDS | Local trouble act Map fault data card 1 L3 |  | 2023-07-02 | 6:00 | Found alarm in fire alarm, lead to inspection of failure identification | 0 | Fire Alarm programming issue | Software | No | N/A | Informed to supplier (Zamil) |  | 2023-07-02 | 6:00
TR-L4-4B1-00025 | FDS | 4B1FDS | Map Fault DataCard1 L7 |  | 2023-07-03 | 8:00 | Alarm idicated from Fire Alarm System | 0 | Due to not properly installed | Software | No | N/A | Fire alarm team will be rectify |  | 2023-07-03 | 8:00