## Sheet1
ID | Project | System | Subsystem | Product id | Product description | Asset type | Asset description | MTBF (hrs) | MTBSAF (hrs) | MTTR (mins) | MART | Asset quantity | Availability target
471 | Riyadh CJV | ICT | ACID | ACID | ACID - Access Control and Intrusion Detection System | ACID | ACID - Access Control and Intrusion Detection System | 701754 | 0 | 30 | 0 | 31 | 99.97
472 | Riyadh CJV | ICT | CCTV | CCTV | CCTV - Closed Circuit Television | CCTV | CCTV - Closed Circuit Television | 32000 | 0 | 30 | 0 | 30 | 99.5
473 | Riyadh CJV | ICT | Telephone / Intercom | INTERCOM | INTERCOM - Inter Communication Unit | INTERCOM | INTERCOM - Inter Communication Unit | 25000 | 0 | 30 | 0 | 31 | 99.99
474 | Riyadh CJV | ICT | Telephone / Intercom | TELEPHONE | TELEPHONE | TELEPHONE | TELEPHONE | 30000 | 0 | 30 | 0 | 31 | 99.99
475 | Riyadh CJV | ICT | Telephone / Intercom | PABX-IPBX | PABX-IPBX - Internet Protocol Private Branch Exchange | PABX-IPBX | PABX-IPBX - Internet Protocol Private Branch Exchange | 50000 | 0 | 30 | 0 | 31 | 99.99
476 | Riyadh CJV | ICT | AUDIO RECORDING | AUDIO RECORDING | AUDIO RECORDING | AUDIO RECORDING | AUDIO RECORDING | 25000 | 0 | 30 | 0 | 31 | 99.5
477 | Riyadh CJV | ICT | ICT LAN | ICT LAN | ICT LAN - Local Area Network | ICT LAN | ICT LAN - Local Area Network | 60000 | 0 | 30 | 0 | 32 | 99.99
478 | Riyadh CJV | LIFT & ESCALATORS | LIFT & ESCALATORS | LIFT | LIFT / ELEVATOR | LIFT | LIFT / ELEVATOR | 2000 | 0 | 1020 | 0 | 18 | 99
479 | Riyadh CJV | LIFT & ESCALATORS | LIFT & ESCALATORS | ES - Escalator | ES - Escalator | ES | ES - Escalator | 2000 | 0 | 600 | 0 | 12 | 99
480 | Riyadh CJV | EME | AHUS | AHUS | AHUS - Air Handling Unit System | AHUS | AHUS - Air Handling Unit System | 2678571 | 0 | 30 | 0 | 14 | 99.998
481 | Riyadh CJV | EME | AIC | AIC | AIC - Air Curtain | AIC | AIC - Air Curtain | 2678571 | 0 | 30 | 0 | 16 | 99.998
482 | Riyadh CJV | EEL | CBS | CBS | CBS - Central Battery System | CBS | CBS - Central Battery System | 100000 | 0 | 30 | 0 | 29 | 99
483 | Riyadh CJV | EME | CHILLER | CHILLER | CHILLER | CHILLER | CHILLER | 2678571 | 0 | 30 | 0 | 14 | 99.998
484 | Riyadh CJV | EME | CPM | CPM | CPM - Chiller Plant Manager | CPM | CPM - Chiller Plant Manager | 2678571 | 0 | 30 | 0 | 14 | 99
485 | Riyadh CJV | EME | CWS | CWS | CWS - Chilled Water System | CWS | CWS - Chilled Water System | 2678571 | 0 | 30 | 0 | 14 | 98
486 | Riyadh CJV | EPH | DWS | DWS | DWS - Domestic Water System | DWS | DWS - Domestic Water System | 80000 | 0 | 30 | 0 | 25 | 97
487 | Riyadh CJV | EPH | EWH | EWH | EWH - Water heater | EWH | EWH - Water heater | 32000 | 0 | 15 | 0 | 22 | 97
488 | Riyadh CJV | EME | FAN | FAN | FAN - Ventilation Fan | FAN | FAN - Ventilation Fan | 2678571 | 0 | 30 | 0 | 35 | 99
489 | Riyadh CJV | EME | FCU | FCU | FCU - Fan Coil Unit | FCU | FCU - Fan Coil Unit | 2678571 | 0 | 30 | 0 | 24 | 99
490 | Riyadh CJV | EFP | FDS | FDS | FDS - Fire Detection System | FDS | FDS - Fire Detection System | 120000 | 0 | 30 | 0 | 31 | 99
491 | Riyadh CJV | EFP | FM200 | FM200 | FM200 - Clean Agent Fire Suppression System | FM200 | FM200 - Clean Agent Fire Suppression System | 70000 | 0 | 20 | 0 | 38 | 98.5
492 | Riyadh CJV | EFP | FOMSS | FOMSS | FOMSS - Foam Suppression System | FOMSS | FOMSS - Foam Suppression System | 70000 | 0 | 20 | 0 | 21 | 98.5
493 | Riyadh CJV | EFP | FPUMP (BUILD) | FPUMP (BUILD) | FPUMP (BUILD) - Fire Pump | FPUMP (BUILD) | FPUMP (BUILD) - Fire Pump | 90000 | 0 | 35 | 0 | 20 | 99
494 | Riyadh CJV | EPH | FS | FS | FS - Fuel System | FS | FS - Fuel System | 85000 | 0 | 30 | 0 | 28 | 99
495 | Riyadh CJV | EEL | GEN | GEN | GEN - GENERATOR | GEN | GEN - GENERATOR | 100000 | 0 | 35 | 0 | 27 | 99
496 | Riyadh CJV | EPH | IS | IS | IS - Irrigation Water System | IS | IS - Irrigation Water System | 35000 | 0 | 30 | 0 | 6 | 97.5
497 | Riyadh CJV | EEL | LCS | LCS | LCS - Light control System | LCS | LCS - Light control System | 134368 | 0 | 30 | 0 | 22 | 99
498 | Riyadh CJV | EEL | LDP | LDP | LDP - Light Distribution Panel | LDP | LDP - Light Distribution Panel | 134368 | 0 | 30 | 0 | 34 | 99
499 | Riyadh CJV | EEL | MCC | MCC | MCC - Motor Control Centre | MCC | MCC - Motor Control Centre | 134368 | 0 | 30 | 0 | 25 | 98.5
500 | Riyadh CJV | TMS | MISTING | MISTING | MISTING | MISTING | MISTING | 75000 | 0 | 30 | 0 | 4 | 99
501 | Riyadh CJV | EEL | PDP | PDP | PDP - Power Distribution Panels | PDP | PDP - Power Distribution Panels | 134368 | 0 | 30 | 0 | 35 | 99
502 | Riyadh CJV | EME | PFAN | PFAN | PFAN - Pressurisation Fans System | PFAN | PFAN - Pressurisation Fans System | 2678571 | 0 | 30 | 0 | 23 | 99
503 | Riyadh CJV | EEL | PFC | PFC | PFC - PFC System | PFC | PFC - PFC System | 45000 | 0 | 30 | 0 | 28 | 97
504 | Riyadh CJV | EME | SEXF | SEXF | SEXF - Smoke extraction fan system | SEXF | SEXF - Smoke extraction fan system | 2678571 | 0 | 30 | 0 | 20 | 99
505 | Riyadh CJV | EPH | SFDS | SFDS | SFDS - Sump Force Drainage System | SFDS | SFDS - Sump Force Drainage System | 50000 | 0 | 30 | 0 | 26 | 97
506 | Riyadh CJV | EPH | TFDS | TFDS | TFDS - Tunnel Fire Detection System | TFDS | TFDS - Tunnel Fire Detection System | 50000 | 0 | 30 | 0 | 3 | 97
507 | Riyadh CJV | TMS | TMCS | TMCS | TMCS - Tunnel Monitoring and Control system | TMCS | TMCS - Tunnel Monitoring and Control system | 100000 | 0 | 30 | 0 | 4 | 99
508 | Riyadh CJV | TMS | TVF | TVF | TVF - Tunnel Ventilation Fans | TVF | TVF - Tunnel Ventilation Fans | 55000 | 0 | 40 | 0 | 3 | 99
509 | Riyadh CJV | EEL | UPS | UPS | UPS - Uninterrupted Power Supply System | UPS | UPS - Uninterrupted Power Supply System | 100000 | 0 | 35 | 0 | 28 | 99.99
510 | Riyadh CJV | EME | VRF | VRF | VRF - Variable refrigerant flow System | VRF | VRF - Variable refrigerant flow System | 2678571 | 0 | 30 | 0 | 8 | 97
511 | Riyadh CJV | ICT | BMS | BMS | BMS - Building Management System | BMS | BMS - Building Management System | 55000 | 0 | 30 | 0 | 32 | 99.5
512 | Riyadh CJV | EEL | MDB | MDB | MDB - Main Distibution Board | MDB | MDB - Main Distibution Board | 134368 | 0 | 30 | 0 | 28 | 99
513 | Riyadh CJV | EPH | FRCP | FRCP | Fire Recirculation Pump | FRCP | Fire Recirculation Pump | 698500 | 0 | 30 | 0 | 0 | 98.9
514 | Riyadh CJV | LIFT & ESCALATORS | TRAVELATOR | TRAVELATOR | TRAVELATOR | TRAVELATOR | TRAVELATOR | 25000 | 0 | 750 | 0 | 0 | 99