## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode Id | Date | Time | Detection | Service delay | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
TR-INC_L6_20230601_001 | MISTING | 6H2MISTING | INC_L6_20230601_001:- Activation of the water mist system to cool the stabling position in 6H2 and High pressure pump was not pressurized water mist system while there is emergency mode activated and it is not reached 80 bar pressuer as per the design due to High pressure pump failure. |  | 2023-06-01 | 8:00 | Physically monitor | 20340 | Notification indicated in water mist PLC | Hardware | No | N/A | Replace defective Pump's mechanical seal and piston assembly. Also due to lack of supplier the pump is pending to start. |  | 2023-06-01 | 8:00 | 2023-06-15 | 13:00
TR-INC_L6_20230616_001 | CPM | 6E1CPM | INC_L6_20230616_001:- COM-6E1-CL-001, active chiller alarm in CPM and it has indicated that All chiller have failed / failed to chiller OFF / ON |  | 2023-06-16 | 18:14 | Alarm indication | 136 | Alarm indication in CPM and BMS. | Software | No | N/A | Pending |  | 2023-06-16 | 18:14 | 2023-06-22 | 20:30
TR-INC_L6_20230622_001 | DWS | 6H1DWS | INC_L6_20230622_001:- (Sanitary fixture wash basin) FLOW team has found that there is no water flow in was basin mixture and found that battery has defected and replace new batteries. |  | 2023-06-22 | 8:15 | FLOW team found | 495 | Lack of flow found FLOW team and defected battery replaced | Hardware | No | N/A | Done/ Battery has replace. |  | 2023-06-22 | 8:15 | 2023-06-22 | 16:30