## Sheet2
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay (mins) | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
L4-4E1-00013 | CCTV | 4E1CCTV | CCTV is offline L4E1-CMIN-PL015, L4E1-CMIN-CL002, L4E1-CMIN-CL013, L4E1-CMIN-GL105, L4E1-CFIX-CL106 |  | 01-01-2023 | 08:00:15 | Found alarm in Scada, lead to inspection of failure identification | 18720 | CCTV is offline L4E1-CMIN-PL015, L4E1-CMIN-CL002, L4E1-CMIN-CL013, L4E1-CMIN-GL105, L4E1-CFIX-CL106 | Software | No | N/A | Informed ICT team to rectify |  | 01-02-2023 | 07:00:00 | 14-02-2023 | 17:00:00
L4-4E1-00014 | CCTV | 4E1CCTV | CCTV is damaged |  | 12-09-2021 | 08:00:16 | Found alarm in Scada, lead to inspection of failure identification | 18720 | CCTV is damaged | Hardware | No | N/A | Replaced damaged CCTV |  | 01-02-2023 | 08:00:00 | 14-02-2023 | 16:00:00
L6-6H1-0011 | FCU | 6H1FCU | The Motor Failure |  | 22-01-2023 | 08:05:11 | The Motor Burned | 24780 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 01-10-2022 | 08:00:00 | 18-10-2022 | 11:00:00
L4-4E1-00001 | FDS | 4E1FDS | Fire Alarm Fault related to MSFD as Manual Pull station damaged |  | 01-03-2023 | 08:01:18 | found alarm in FACP. Lead to physical inspection of failure identification | 1800 | Fire Alarm Fault related to MSFD as Manual Pull station damaged | Hardware | No | N/A | Replaced MPS |  | 04-01-2023 | 08:00:00 | 05-01-2023 | 10:00:00
L6-6G1-0017 | SEXF | 6G1SEXF | FAN MOTOR Failure |  | 15-01-2023 | 08:04:12 | The Motor Burned | 16140 | FAN MOTOR Failure | Hardware | No | N/A | FAN REPLACED |  | 04-01-2023 | 08:00:00 | 15-01-2023 | 11:00:00
L6-6D2-0025 | DWS | 6D2DWS | Shaft Seal Leakage |  | 04-01-2023 | 08:03:03 | during daily cartaking activites found leakage | 8760 | Shaft Seal Leakage | Hardware | No | N/A | Repaired |  | 06-02-2023 | 08:00:00 | 12-02-2023 | 14:00:00
L4-4E1-00008 | GEN | 4E1GEN | Generator engine oil leaked |  | 16-01-2023 | 08:01:25 | Found alarm in Scada, lead to inspection of failure identification and also generator got OF during power shutdown by TSY | 1380 | Generator engine oil leaked | Hardware | No | N/A | Cleaned generator components & internal piping, fill engine oil |  | 06-02-2023 | 10:00:00 | 07-02-2023 | 15:00:00
L4-4C1-00015 | SEXF | 4C1SEXF | SEF Motor winding got damaged due to wrong termination |  | 15-09-2022 | 08:00:42 | Alarm in BMS system, lead to physical inspection of failure identification | 4380 | SEF Motor winding got damaged due to wrong termination | Hardware | No | N/A | Sent motor to workshop for rewinding |  | 06-02-2023 | 08:00:00 | 09-02-2023 | 15:00:00
L4-4B1-00025 | FDS | 4B1FDS | Map Faul DataCard 1 L1 |  | 20-02-2023 | 08:00:25 | Monitoring from Fire Alarm System | 2820 | Map Faul DataCard 1 L1 | Software | No | N/A | Informed Zamil team to check rectify these issues |  | 07-03-2023 | 08:00:00 | 09-03-2023 | 17:00:00
L4-4B1-00026 | FDS | 4B1FDS | Map Faul DataCard 1 L7 |  | 12-03-2023 | 08:00:26 | Monitoring from Fire Alarm System | 2820 | Map Faul DataCard 1 L7 | Software | No | N/A | Informed Zamil team to check rectify these issues |  | 07-03-2023 | 08:00:00 | 09-03-2023 | 17:00:00
L6-6D2-0028 | ICT LAN | 6D2ICT LAN | full line 4&6switches full DCS link Down |  | 08-09-2022 | 08:00:48 | no communication with OCC | 1042 | full line 4&6switches full DCS link Down | Hardware | No |  | manually reanabling all DCS links in all locations |  | 09-02-2022 | 14:49:00 | 10-02-2022 | 15:49
L4-4E1-00006 | GEN | 4E1GEN | Generator is OFF |  | 16-01-2023 | 08:01:23 | Found alarm in Scada, lead to inspection of failure identification | 1665 | Generator is OFF | Hardware | No | N/A | Replaced Batteries |  | 10-01-2023 | 09:15:00 | 11-01-2023 | 11:00:00
L4-4C1-00007 | CCTV | 4C1CCTV | 14 CCTV Camera are not working 11 CCTV's are offline &3 CCTV's need to configured by ICT Team) L4C1-CM-PL-006 L4C1-CM-PL-008 L4C1-CM-PL-010 L4C1-CFIX-GL015 L4C1-CFIX-PL-004 L4C1-CFIX-CL110 L4C1-CMIN-CL012 L4C1-CMIN-GL001 L4C1-CMIN-GL003 L4C1-CMIN-GL005 L4C1-CMIN-CL101 L4C1-CMIN-CL102 L4C1-CMIN-GL015 |  | 19-02-2023 | 08:00:09 | Alarm indicated in Scada/ISM System | 1770 | 14 CCTV Camera are not working 11 CCTV's are offline &3 CCTV's need to configured by ICT Team) L4C1-CM-PL-006 L4C1-CM-PL-008 L4C1-CM-PL-010 L4C1-CFIX-GL015 L4C1-CFIX-PL-004 L4C1-CFIX-CL110 L4C1-CMIN-CL012 L4C1-CMIN-GL001 L4C1-CMIN-GL003 L4C1-CMIN-GL005 L4C1-CMIN-CL101 L4C1-CMIN-CL102 L4C1-CMIN-GL015 | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV |  | 11-02-2023 | 09:00:00 | 12-02-2023 | 09:30:00
L4-4B1-00014 | INTERCOM | 4B1INTERCOM | Intercom not working |  | 25-02-2023 | 08:00:41 | Monitoring from SCADA/ACID System | 9596 | Intercom not working | Software | No | N/A | Rectify by site team |  | 11-02-2023 | 12:04:00 | 18-02-2023 | 20:00:00
L6-6G2-0016 | ACID | 6G2ACID | SIL2 sensor activated |  | 21-01-2023 | 08:00:54 | TSY-SCADA System | 14880 | SIL2 sensor activated | Software | No |  | fixed in its location |  | 11-10-2022 | 08:00:00 | 21-10-2022 | 08:00:00
L6-6G2-0001 | CWS | 6G2CWS | Mechanical Seal Failure |  | 15-11-2022 | 08:04:29 | overheat and noise of pump | 1620 | Mechanical Seal Failure | Hardware | No | N/A | Mechanical Seal replaced |  | 12-01-2022 | 09:00:00 | 13-01-2022 | 12:00:00
L6-6D2-0003 | SEXF | 6D2SEXF | FAN MOTOR Failure |  | 26-07-2022 | 08:02:41 | The Motor Burned | 7380 | FAN MOTOR Failure | Hardware | No | N/A | FAN REPLACED |  | 12-09-2021 | 09:00:00 | 17-09-2021 | 12:00:00
L6-6G2-0008 | FCU | 6G2FCU | PLC board Failure |  | 25-01-2023 | 08:04:36 | The PLC board malfunction | 1740 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 14-07-2022 | 08:00:00 | 2022-07-15 | 11:00:00
L6-6G1-0003 | FAN | 6G1FAN | FAN MOTOR Failure |  | 21-02-2023 | 08:03:58 | The Motor Burned | 1740 | FAN MOTOR Failure | Hardware | No | N/A | rewind the motor |  | 14-09-2022 | 08:00:00 | 15-09-2022 | 11:00:00
L4-4E1-00004 | FDS | 4E1FDS | Appeared mapping fault MFACP-4E1-02 |  | 16-01-2023 | 08:01:21 | Found alarm in Scada, lead to inspection of failure identification | 1620 | Appeared mapping fault MFACP-4E1-02 | Software | No | N/A | Informed to FA team |  | 15-01-2023 | 07:00:00 | 16-01-2023 | 14:00:00
L6-6D2-0004 | SEXF | 6D2SEXF | FAN MOTOR Failure |  | 30-07-2022 | 08:02:42 | The Motor Burned | 4620 | FAN MOTOR Failure | Hardware | No | N/A | FAN REPLACED |  | 15-09-2021 | 08:00:00 | 18-09-2021 | 11:00:00
L6-6D2-0006 | FCU | 6D2FCU | The Motor Failure |  | 12-10-2022 | 08:02:44 | The Motor Burned | 1740 | The Motor Failure | Hardware | No | N/A | motor replaced by supplier |  | 15-11-2021 | 08:00:00 | 2021-11-16 | 11:00:00
L6-6H1-0017 | SFDS | 6H1SFDS | The Level Sensor Failure |  | 04-05-2022 | 08:05:17 | during daily cartaking activites found the water level fluctuation | 1740 | The Level Sensor Failure | Hardware | No | N/A | Level Sensor replaced |  | 15-11-2022 | 08:00:00 | 2022-11-16 | 11:00:00
L6-6G2-0006 | FCU | 6G2FCU | The Transformer Failure |  | 12-01-2023 | 08:04:34 | The Transformer Burned | 1620 | The Transformer Failure | Hardware | No | N/A | Transformer replaced |  | 16-06-2022 | 09:00:00 | 2022-06-17 | 12:00:00
L6-C&C6.4-0004 | ACID | 6H2ACID | SIL2 sensor activated |  | 31-01-2023 | 08:00:57 | TSY-SCADA System | 6240 | SIL2 sensor activated | Software | No |  | fixed in the software |  | 16-10-2022 | 08:00:00 | 20-10-2022 | 08:00:00
L4-4G1-00026 | CCTV | 4G1CCTV | 10- CCTV are offline in ism system. L4G1-CFIX-GL-104.103,102,101,07,006,004,002,001 |  | 01-11-2022 | 08:00:47 | Monitoring from SCADA/ ISM System | 1440 | 10- CCTV are offline in ism system. L4G1-CFIX-GL-104.103,102,101,07,006,004,002,001 | Hardware | No | N/A | informed ICT TEAM |  | 18-02-2023 | 08:00:00 | 19-02-2023 | 16:00:00
L4-4D1-00014 | GEN | 4D1GEN | Generator stopped suddenly |  | 26-02-2023 | 08:01:10 | Found during Physical Inspection | 1620 | Generator stopped suddenly | Hardware | No | N/A | Oil Replaced & done general overall maintenance |  | 18-02-2023 | 08:00:00 | 19-02-2023 | 13:00:00
L4-4B1-00009 | INTERCOM | 4B1INTERCOM | Intercom not working |  | 20-02-2023 | 08:00:40 | Monitoring from SCADA/ACID System | 4460 | Intercom not working | Software | No | N/A | Informed ICT team to rectify the INTERCOM |  | 18-02-2023 | 04:40:00 | 21-02-2023 | 17:00:00
L6-6G2-0015 | SEXF | 6G2SEXF | FAN MOTOR Failure |  | 20-01-2023 | 08:04:43 | The Motor Burned | 16140 | FAN MOTOR Failure | Hardware | No | N/A | rewind the motor |  | 18-10-2022 | 08:00:00 | 29-10-2022 | 11:00:00
L6-6H1-0026 | FS | 6H1FS | Bulk tank high water level alarm |  | 30-01-2023 | 08:05:26 | BMS alarm | 10380 | Bulk tank high water level alarm | Hardware | No | N/A | reported by supplier and SAMNAN rectified |  | 18-12-2022 | 08:00:00 | 25-12-2022 | 11:00:00
L6-6E1-0002 | FAN | 6E1FAN | FAN MOTOR Failure |  | 11-10-2022 | 08:03:07 | The Motor Burned | 11820 | FAN MOTOR Failure | Hardware | No | N/A | rewind the motor |  | 19-05-2021 | 08:00:00 | 27-05-2021 | 11:00:00
L6-6G2-0009 | SFDS | 6G2SFDS | The Level Sensor Failure |  | 27-01-2023 | 08:04:37 | during T&C found the water level fluctuation | 3060 | The Level Sensor Failure | Hardware | No | N/A | Level Sensor replaced |  | 20-07-2022 | 09:00:00 | 2022-07-22 | 12:00:00
L6-6H1-0008 | FCU | 6H1FCU | PLC board Failure |  | 19-01-2023 | 08:05:08 | The PLC board malfunction | 3060 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 20-08-2022 | 09:00:00 | 2022-08-22 | 12:00:00
L6-6G1-0008 | FCU | 6G1FCU | PLC & PCB board Failure |  | 12-02-2023 | 08:04:03 | The PCB & PCB board Burned | 3180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 20-10-2022 | 08:00:00 | 2022-10-22 | 11:00:00
L4-4E1-00027 | FCU | 4E1FCU | Dirty Filter |  | 02-01-2023 | 08:01:44 | Found alarm in BMS, lead to inspection of failure identification | 420 | Dirty Filter | Hardware | No | N/A | Assigned care taking team to clean |  | 21-02-2023 | 08:00:00 | 21-02-2023 | 9:00
L6-6E1-0005 | FCU | 6E1FCU | The Motor Failure |  | 16-02-2023 | 08:03:10 | The Motor Burned | 6060 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 21-09-2021 | 08:00:00 | 2021-09-25 | 11:00:00
L6-6G1-0033 | CWS | 6G1CWS | the bearing Failure |  | 10-01-2023 | 08:05:18 | overheat and noise of pump | 1620 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 21-11-2022 | 08:00:00 | 22-11-2022 | 13:00:00
L6-6G1-0034 | CWS | 6G1CWS | the bearing Failure |  | 12-01-2023 | 08:05:19 | overheat and noise of pump | 3180 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 21-11-2022 | 08:00:00 | 23-11-2022 | 11:00:00
L6-6G1-0035 | CWS | 6G1CWS | the bearing Failure |  | 14-01-2023 | 08:05:20 | overheat and noise of pump | 3180 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 21-11-2022 | 08:00:00 | 23-11-2022 | 11:00:00
L6-6E1-0010 | FOMSS | 6E1FOMSS | Resistance Failure |  | 23-01-2023 | 08:03:15 | during fire scenario test there are no alarm on fire alarm panel | 4620 | Resistance Failure | Hardware | Yes | SRIL_CJV_083 | reported by supplier and ETECHS rectified |  | 21-12-2022 | 08:00:00 | 24-12-2022 | 11:00:00
L4-4E1-00007 | FDS | 4E1FDS | CT device damaged for SEF-4E1-CL-11 MFACP-4E1-CL-02 |  | 16-01-2023 | 08:01:24 | Found alarm in Scada, lead to inspection of failure identification | 1860 | CT device damaged for SEF-4E1-CL-11 MFACP-4E1-CL-02 | Software | No | N/A | Replaced CT device |  | 22-01-2023 | 07:00:00 | 23-01-2023 | 10:00:00
L6-6F1-0001 | FCU | 6F1FCU | The Motor Failure |  | 02-02-2023 | 08:03:30 | The Motor Burned | 1740 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 22-06-2021 | 08:00:00 | 2021-06-23 | 11:00:00
L6-6G2-0007 | FCU | 6G2FCU | PLC board Failure |  | 21-01-2023 | 08:04:35 | The PLC board malfunction | 5940 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 22-06-2022 | 09:00:00 | 2022-06-26 | 12:00:00
L6-ITPS 6.1-0001 | UPS | ITPS6.1UPS | 6D2 UPS Interruption due to unstable incoming power from MV Source (UPS Rectifier Out of Tolerance) |  | 14-01-2023 | 08:06:02 | the rectifier incoming from TSY side is out of tolerance and the UPS connected load was also out of accepted tolerance so the UPS Invertor switched off | 4620 | 6D2 UPS Interruption due to unstable incoming power from MV Source (UPS Rectifier Out of Tolerance) | Hardware | No | N/A | UPS power restored |  | 24-02-2022 | 21:01:00 | 2022-02-28 | 22:06
L6-6G2-0010 | FCU | 6G2FCU | The Motor Failure |  | 28-01-2023 | 08:04:38 | The Motor Burned | 1620 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 24-07-2022 | 09:00:00 | 2022-07-25 | 12:00:00
L6-6H1-0021 | CWS | 6H1CWS | the bearing Failure |  | 15-01-2023 | 08:05:21 | overheat and noise of pump | 1740 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 24-11-2022 | 08:00:00 | 25-11-2022 | 11:00:00
L6-6H1-0022 | CWS | 6H1CWS | the bearing Failure |  | 16-01-2023 | 08:05:22 | overheat and noise of pump | 3173 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 24-11-2022 | 08:00:00 | 26-11-2022 | 11:00:00
L6-6H1-0023 | CWS | 6H1CWS | the bearing Failure |  | 24-01-2023 | 08:05:23 | overheat and noise of pump | 4620 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 24-11-2022 | 08:00:00 | 27-11-2022 | 11:00:00
L6-6D2-0014 | FS | 6D2FS | Fault-Magnetic insulation error |  | 29-09-2022 | 08:02:52 | BMS alarm | 1740 | Fault-Magnetic insulation error | Hardware | No | N/A | reported by supplier and SAMNAN rectified |  | 25-12-2022 | 08:00:00 | 2022-12-26 | 11:00:00
L4-4E1-00011 | FCU | 4E1FCU | Motor damaged |  | 31-01-2023 | 08:01:28 | Physical inspection lead to the failure identification | 2940 | Motor damaged | Hardware | No | N/A | Replaced blower motor |  | 26-01-2023 | 09:00:00 | 28-01-2023 | 14:00:00
L4-4C1-00021 | FCU | 4C1FCU | Showing Dirty Filter Alarm in BMS system FCU-4C1-CL-029 & 039 |  | 09-10-2022 | 08:00:48 | Alarm indicated in Scada/BMS System | 41580 | Showing Dirty Filter Alarm in BMS system FCU-4C1-CL-029 & 039 | Hardware | No | N/A | Informed to BMS team to check and rectify |  | 26-02-2023 | 13:00:00 | 27-03-2023 | 14:00
L6-6F1-0004 | SEXF | 6F1SEXF | FAN MOTOR Failure |  | 08-12-2022 | 08:03:33 | The Motor Burned | 3060 | FAN MOTOR Failure | Hardware | No | N/A | FAN REPLACED |  | 26-09-2022 | 09:00:00 | 28-09-2022 | 12:00:00
L6-6H1-0016 | FCU | 6H1FCU | PLC board Failure |  | 31-01-2023 | 08:05:16 | The PLC board malfunction | 3180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 26-10-2022 | 08:00:00 | 2022-10-28 | 11:00:00
L6-6E1-0008 | SEXF | 6E1SEXF | FAN MOTOR Failure |  | 31-01-2023 | 08:03:13 | The Motor Burned | 1620 | FAN MOTOR Failure | Hardware | No | N/A | rewind the motor |  | 27-01-2022 | 09:00:00 | 28-01-2022 | 12:00:00
L6-6D2-0002 | CHILLER | 6D2CHILLER | The Chiller compressor Failure |  | 24-07-2022 | 08:02:40 | there was alarms and chiller tripping many times | 1500 | The Chiller compressor Failure | Hardware | No | N/A | Repairing chiller compressor |  | 29-07-2021 | 10:00:00 | 2021-07-30 | 13:00:00
L6-6H1-0010 | FCU | 6H1FCU | The Motor Failure |  | 21-01-2023 | 08:05:10 | The Motor Burned | 1740 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 29-09-2022 | 08:00:00 | 2022-09-30 | 11:00:00
L6-6G2-0013 | FCU | 6G2FCU | The Motor Failure |  | 31-01-2023 | 08:04:41 | The Motor Burned | 1620 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 30-08-2022 | 09:00:00 | 2022-08-31 | 12:00:00
L6-6G2-0019 | AHUS | 6G2AHUS | the bearing Failure |  | 28-01-2023 | 08:04:47 | Noise | 180 | the bearing Failure | Hardware | No | N/A | change bearing by TRANE and rebalancing for blower |  | 01-01-2023 | 08:00:00 | 2023-01-01 | 11:00:00
L6-6D2-0018 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 08-10-2022 | 08:02:56 | during daily checking of UPS it was observed in (alarms Log) | 210 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 08:00:00 | 01-02-2022 | 11:30:00
L6-6E1-0015 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 08-02-2023 | 08:03:20 | during daily checking of UPS it was observed in (alarms Log) | 180 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 20:11:00 | 01-02-2022 | 23:11:00
L6-6E1-0016 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 09-02-2023 | 08:03:21 | during daily checking of UPS it was observed in (alarms Log) | 123 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 13:50:00 | 01-02-2022 | 15:53:00
L6-6E1-0017 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 27-02-2023 | 08:03:22 | during daily checking of UPS it was observed in (alarms Log) | 120 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 08:00:00 | 01-02-2022 | 10:00:00
L6-6E1-0018 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 05-02-2023 | 08:03:23 | during daily checking of UPS it was observed in (alarms Log) | 120 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 09:29:00 | 01-02-2022 | 11:29:00
L6-6E1-0019 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 02-05-2023 | 08:03:24 | during daily checking of UPS it was observed in (alarms Log) | 17 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 10:17:00 | 01-02-2022 | 10:34:00
L6-6E1-0020 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2023 | 08:03:25 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 08:00:00 | 01-02-2022 | 12:00:00
L6-6E1-0021 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 14-01-2023 | 08:03:26 | during daily checking of UPS it was observed in (alarms Log) | 150 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2022 | 09:00:00 | 01-02-2022 | 11:30:00
L4-4C1-00009 | FCU | 4C1FCU | FCU Filters showing dirty - FCU-4C1-GL-006A |  | 28-02-2023 | 08:00:36 | Alarm indicated in Scada/BMS System | 480 | FCU Filters showing dirty - FCU-4C1-GL-006A | Hardware | No | N/A | Cleaned the Filters |  | 01-02-2023 | 08:00:00 | 01-02-2023 | 16:00:00
L4-4D1-00021 | FCU | 4D1FCU | Not working in Manual & auto Mode |  | 01-03-2023 | 08:01:17 | Physical inspection lead to the failure identification | 120 | Not working in Manual & auto Mode | Hardware | No | N/A | PR raised for maintenance |  | 01-02-2023 | 07:00:00 | 01-02-2023 | 09:00:00
L4-4E1-00012 | FCU | 4E1FCU | Dirty Filter FCU-4E1-CL-13, FCU-4E1-CL-14 |  | 05-02-2023 | 08:01:29 | Found alarm in BMS, lead to inspection of failure identification | 60 | Dirty Filter FCU-4E1-CL-13, FCU-4E1-CL-14 | Hardware | No | N/A | Assigned care taking team to clean |  | 01-02-2023 | 07:00:00 | 01-02-2023 | 8:00
L6-6H2-0011 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 25-01-2023 | 08:05:48 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-02-2023 | 00:00:00 | 01-02-2023 | 00:30:00
L6-6G1-0031 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 16-10-2022 | 08:04:26 | during daily checking of UPS it was observed in (alarms Log) | 122.3833 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 01-03-2022 | 05:58:00 | 01-03-2022 | 08:00:23
L4-4E1-00030 | ES | 4E1ES | Not working |  | 06-01-2023 | 08:00:37 | Found alarm in Scada, lead to inspection of failure identification | 90 | Not working | Hardware | No | N/A | Informed Elec team |  | 01-03-2023 | 07:30:00 | 01-03-2023 | 09:00:00
L6-6F1-0002 | FCU | 6F1FCU | The Motor Failure |  | 13-02-2023 | 08:03:31 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 01-06-2022 | 09:00:00 | 2022-06-01 | 12:00:00
L6-6G1-0012 | FCU | 6G1FCU | The Transformer Failure |  | 04-07-2022 | 08:04:07 | The Transformer Burned | 180 | The Transformer Failure | Hardware | No | N/A | Transformer replaced |  | 01-11-2022 | 08:00:00 | 2022-11-01 | 11:00:00
L6-6H1-0024 | FPUMP (BUILD) | 6H1FPUMP (BUILD) | Rubber Failure |  | 27-01-2023 | 08:05:24 | during daily cartaking activites found rubber damage | 180 | Rubber Failure | Hardware | No | N/A | Rubber replaced |  | 01-12-2022 | 08:00:00 | 01-12-2022 | 11:00:00
L6-6H2-0012 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 27-01-2023 | 08:05:49 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 02-02-2023 | 01:00:00 | 02-02-2023 | 01:30:00
L6-6G1-0032 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-11-2022 | 08:04:27 | during daily checking of UPS it was observed in (alarms Log) | 62.4 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 02-03-2022 | 06:58:00 | 02-03-2022 | 08:00:24
L4-4C1-000023 | ACID | 4C1ACID | Door not opening with card |  | 21-11-2022 | 08:00:02 | Alarm not indicated in scada/ACID system, lead to physical inspection of failure indentification | 60 | Door not opening with card | Software | No | N/A | Informed ICT team to rectify |  | 02-03-2023 | 08:00:00 | 02-03-2023 | 09:00:00
L4-4E1-00035 | ACID | 4E1ACID | Doors are open from the ACID system - AC-4E1-CL-024 - AC-4E1-CL-025 - AC-4E1-CL-026 - AC-4E1-CL-027 - AC-4E1-CL-028 - AC-4E1-CL-029 - AC-4E1-CL-102 |  | 14-02-2023 | 08:00:35 | Physical inspection lead to the failure identification | 480 | Doors are open from the ACID system - AC-4E1-CL-024 - AC-4E1-CL-025 - AC-4E1-CL-026 - AC-4E1-CL-027 - AC-4E1-CL-028 - AC-4E1-CL-029 - AC-4E1-CL-102 | Software | No | N/A | Informed ICT team to rectify |  | 02-03-2023 | 08:00:00 | 02-03-2023 | 16:00:00
L4-4E1-00031 | INTERCOM | 4E1INTERCOM | Offline |  | 06-01-2023 | 08:00:45 | Found alarm in Scada, Compared ACID, lead to inspection of failure identification | 60 | Offline | Software | No | N/A | Informed ICT team to rectify |  | 02-03-2023 | 10:00:00 | 02-03-2023 | 11:00:00
L4-4G1-00033 | LCS | 4G1LCS | BMS RECTIFICATION |  | 22-06-2022 | 08:02:38 | Monitoring from SCADA/bms System | 60 | BMS RECTIFICATION | Software | No | N/A | Informed BMS team to rectify |  | 02-03-2023 | 10:00:00 | 02-03-2023 | 11:00:00
L4-4G1-00019 | LDP | 4G1LDP | LDP-CL-1E\2E\5C- Monitor incoming breakers position set to closed (TMCS-Command issue) |  | 04-10-2022 | 08:02:24 | Monitoring from SCADA/ BMSstem | 130 | LDP-CL-1E\2E\5C- Monitor incoming breakers position set to closed (TMCS-Command issue) | Hardware | No | N/A | TSY |  | 02-03-2023 | 10:00:00 | 02-03-2023 | 12:10:00
L4-4C1-00002 | MCC | 4C1MCC | VFD not working -CHWP-4C1-CL-003,006,005 |  | 01-02-2023 | 08:00:29 | Physical inspection lead to the failure identification | 75 | VFD not working -CHWP-4C1-CL-003,006,005 | Hardware | No | N/A | Informed Electrical team to META to solve the issue |  | 02-03-2023 | 10:00:00 | 02-03-2023 | 11:15:00
L6-6G1-0004 | FCU | 6G1FCU | PLC & PCB board Failure |  | 08-02-2023 | 08:03:59 | The PCB & PCB board Burned | 180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 02-10-2022 | 08:00:00 | 02-10-2022 | 11:00:00
L6-6E1-0014 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2023 | 08:03:19 | during daily checking of UPS it was observed in (alarms Log) | 360 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 03-02-2022 | 08:00:00 | 03-02-2022 | 14:00:00
L6-6ITPS-0001 | UPS | ITPS6.1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 28-01-2023 | 08:05:50 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 03-02-2023 | 02:00:00 | 03-02-2023 | 02:30:00
L4-4C1-00011 | FCU | 4C1FCU | FCU & FAHU Filters showing dirty -FAHU-4C1-CL-001 showwing |  | 26-02-2023 | 08:00:38 | Alarm indicated in Scada/BMS System | 480 | FCU & FAHU Filters showing dirty -FAHU-4C1-CL-001 showwing | Hardware | No | N/A | Cleaned the Filters |  | 04-02-2023 | 08:00:00 | 04-02-2023 | 16:00:00
L4-4G1-00022 | FDS | 4G1FDS | GENERAL FAULT DUE TO RAIN |  | 20-10-2022 | 08:02:27 | Monitoring from SCADA/ Fire Alarm PANEL | 360 | GENERAL FAULT DUE TO RAIN | Hardware | No | N/A | device cleaned |  | 04-02-2023 | 10:00:00 | 04-02-2023 | 16:00:00
L4-4G1-00020 | GEN | 4G1GEN | GEN-4G1-CL-001 & 002 Minor Alarm set to fault _Communication issue for BMS |  | 05-10-2022 | 08:02:25 | Monitoring from SCADA/ BMS system | 240 | GEN-4G1-CL-001 & 002 Minor Alarm set to fault _Communication issue for BMS | Hardware | No | N/A | BMS |  | 04-02-2023 | 10:00:00 | 04-02-2023 | 14:00:00
L4-4C2-00001 | MISTING | 4C2MISTING | False Alarm |  | 02-01-2023 | 08:01:55 | BMS and SCADA alarms. | 120 | False Alarm | Software | No | N/A | To be reset by WMS/TMCS |  | 04-02-2023 | 07:00:00 | 04-02-2023 | 09:00:00
L4-4G1-00021 | MISTING | 4G1MISTING | mist system general fault alarms- due to power shutdown and( AEU) Device system is off |  | 12-10-2022 | 08:02:26 | Monitoring from SCADA/ BMS system | 240 | mist system general fault alarms- due to power shutdown and( AEU) Device system is off | Hardware | No | N/A | Panel turned on mannually |  | 04-02-2023 | 10:00:00 | 04-02-2023 | 14:00:00
L6-6G2-0020 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 29-01-2023 | 08:04:48 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 04-02-2023 | 10:00:00 | 04-02-2023 | 14:00:00
L6-6ITPS-0002 | UPS | ITPS6.1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2023 | 08:05:51 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 04-02-2023 | 03:00:00 | 04-02-2023 | 03:30:00
L6-ITPS 6.1-0002 | UPS | ITPS6.1UPS | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation |  | 10-03-2022 | 08:06:03 | all power off in the station | 240 | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation | Hardware | No | N/A | reported to TOO battery tested find 9 pices is dameged |  | 04-02-2023 | 10:00:00 | 04-02-2023 | 14:00:00
L4-4D1-00011 | INTERCOM | 4D1INTERCOM | INTERCOM(INT-CL-022) Required Configuration |  | 06-02-2023 | 08:00:43 | Found in SCADA Alarms | 150 | INTERCOM(INT-CL-022) Required Configuration | Software | No | N/A | Informed ICT team to configure intercom |  | 04-03-2023 | 08:30:00 | 04-03-2023 | 11:00:00
L6-6G2-0004 | UPS | 6G2UPS | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation |  | 26-02-2023 | 08:04:32 | all power off in the station | 240 | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation | Hardware | No | N/A | UPS power restored |  | 04-05-2022 | 15:00:00 | 04-05-2022 | 19:00:00
L6-6H1-0002 | UPS | 6H1UPS | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation |  | 31-01-2023 | 08:05:02 | all power off in the station | 240 | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation | Hardware | No | N/A | UPS power restored |  | 04-05-2022 | 15:00:00 | 04-05-2022 | 19:00:00
L6-6F1-0010 | SFDS | 6F1SFDS | The Controller Failure |  | 23-02-2023 | 08:03:39 | BMS alarm | 180 | The Controller Failure | Hardware | No | N/A | reported by supplier and need to change the controller |  | 04-07-2022 | 08:00:00 | 04-07-2022 | 11:00:00
L6-6H2-0001 | TVF | 6H2TVF | The pcb card Failure |  | 31-01-2023 | 08:05:38 | from control panel send command for open MSFD but no response | 180 | The pcb card Failure | Hardware | No | N/A | rectified the pcb card |  | 04-07-2022 | 08:00:00 | 04-07-2022 | 11:00:00
L6-6G1-0005 | FCU | 6G1FCU | PLC & PCB board Failure |  | 01-02-2023 | 08:04:00 | The PCB & PCB board Burned | 180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 04-10-2022 | 08:00:00 | 04-10-2022 | 11:00:00
L6-6H1-0012 | FCU | 6H1FCU | The Motor Failure |  | 24-01-2023 | 08:05:12 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 04-10-2022 | 08:00:00 | 04-10-2022 | 11:00:00
L4-4E1-00002 | FDS | 4E1FDS | Fire Alarm Fault related to MSFD because MSFD actuator damaged |  | 19-01-2023 | 08:01:19 | found alarm in FACP. Lead to physical inspection of failure identification | 60 | Fire Alarm Fault related to MSFD because MSFD actuator damaged | Hardware | No | N/A | Replaced MSFD actuator |  | 05-01-2023 | 09:00:00 | 05-01-2023 | 10:00
L6-6D2-0022 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 05-02-2023 | 08:03:00 | during daily checking of UPS it was observed in (alarms Log) | 60 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 05-02-2022 | 08:00:00 | 05-02-2022 | 09:00:00
L6-6G1-0016 | MCC | 6G1MCC | VFD breaker Failure |  | 21-12-2021 | 08:04:11 | Physical inspection lead to the failure identification | 240 | VFD breaker Failure | Hardware | No | N/A | Reported to our specialist supplier (META) |  | 05-02-2023 | 11:00:00 | 05-02-2023 | 15:00:00
L6-6G2-0021 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 30-01-2023 | 08:04:49 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 05-02-2023 | 11:00:00 | 05-02-2023 | 15:00:00
L6-6ITPS-0003 | UPS | ITPS6.1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 24-02-2022 | 08:05:52 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 05-02-2023 | 04:00:00 | 05-02-2023 | 04:30:00
L6-C&C6.4-0003 | TVF | 6H2TVF | Cam feedback buttons Failure |  | 30-01-2023 | 08:06:00 | during regulating the cams we found feedback buttons Failure | 180 | Cam feedback buttons Failure | Hardware | No | N/A | cam feedback buttons have been changed |  | 05-07-2022 | 08:00:00 | 05-07-2022 | 11:00:00
L6-6G1-0006 | FCU | 6G1FCU | PLC & PCB board Failure |  | 01-02-2023 | 08:04:01 | The PCB & PCB board Burned | 180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 05-10-2022 | 08:00:00 | 05-10-2022 | 11:00:00
L6-6G1-0013 | FCU | 6G1FCU | PLC & PCB board Failure |  | 05-07-2022 | 08:04:08 | The PCB & PCB board Burned | 180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 05-11-2022 | 08:00:00 | 05-11-2022 | 11:00:00
L6-6G2-0002 | FCU | 6G2FCU | PCB board Failure |  | 31-01-2023 | 08:04:30 | The PCB board malfunction | 180 | PCB board Failure | Hardware | No | N/A | PCB board replaced |  | 06-02-2022 | 08:00:00 | 06-02-2022 | 11:00:00
L6-6G2-0003 | FCU | 6G2FCU | PCB board Failure |  | 02-02-2023 | 08:04:31 | The PCB board malfunction | 180 | PCB board Failure | Hardware | No | N/A | PCB board replaced |  | 06-02-2022 | 08:00:00 | 06-02-2022 | 11:00:00
L6-6D2-0023 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 06-02-2023 | 08:03:01 | during daily checking of UPS it was observed in (alarms Log) | 62 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 06-02-2022 | 06:58:00 | 06-02-2022 | 08:00:00
L6-6F1-0014 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 07-01-2023 | 08:03:43 | during daily checking of UPS it was observed in (alarms Log) | 62 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 06-02-2022 | 06:58:00 | 06-02-2022 | 08:00:00
L4-4C1-00012 | ACID | 4C1ACID | DPR room door is not closing due to acid problem |  | 26-02-2023 | 08:00:01 | Alarm indicated in Scada/ACID System | 240 | DPR room door is not closing due to acid problem | Hardware | No | N/A | Instructed ICT team to rectify the door |  | 06-02-2023 | 08:00:00 | 06-02-2023 | 12:00:00
L4-4C1-00013 | FCU | 4C1FCU | FCU & FAHU Filters showing dirty -FCU-4C1-CL-039 AHU-4C1-CL-003 AHU-4C1-CL-008 FAHU-4C1-CL-002 |  | 26-02-2023 | 08:00:40 | Alarm indicated in Scada/BMS System | 480 | FCU & FAHU Filters showing dirty -FCU-4C1-CL-039 AHU-4C1-CL-003 AHU-4C1-CL-008 FAHU-4C1-CL-002 | Hardware | No | N/A | Cleaned the Filters |  | 06-02-2023 | 08:00:00 | 2023-02-06 | 16:00:00
L4-4C1-00014 | FCU | 4C1FCU | FCU & AHU Filters showing dirty -FCU-4C1-CL-022 |  | 15-02-2023 | 08:00:41 | Alarm indicated in Scada/BMS System | 480 | FCU & AHU Filters showing dirty -FCU-4C1-CL-022 | Hardware | No | N/A | Cleaned the Filters |  | 06-02-2023 | 08:00:00 | 06-02-2023 | 16:00:00
L4-4C2-00009 | ICT LAN | 4C2ICT LAN | Control panel not working |  | 01-02-2023 | 08:00:38 | BMS. | 60 | Control panel not working | Hardware | No | N/A | FTTP supplier to rectify |  | 06-02-2023 | 08:00:00 | 06-02-2023 | 09:00:00
L6-6H2-0003 | MCC | 6H2MCC | it has been concluded that energizing the panels/motors with current configuration will mostly cause overheat and damage to the AC line reactor |  | 14-01-2023 | 08:05:40 | Physical inspection lead to the failure identification | 240 | it has been concluded that energizing the panels/motors with current configuration will mostly cause overheat and damage to the AC line reactor | Hardware | No | N/A | the circuit shall be re-arranged to be MCCB -> PHF -> AC Line Reactor -> VFD -> Motor |  | 06-02-2023 | 12:00:00 | 06-02-2023 | 16:00:00
L4-4C2-00006 | TFDS | 4C2TFDS | Preset Alarm from Program ( Need Reset) |  | 09-03-2023 | 08:02:00 | SCADA alarms. | 120 | Preset Alarm from Program ( Need Reset) | Software | No | N/A | Zamil to reset from program |  | 06-02-2023 | 09:00:00 | 06-02-2023 | 11:00:00
L6-6G2-0022 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2023 | 08:04:50 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 06-02-2023 | 12:00:00 | 06-02-2023 | 16:00:00
L6-6ITPS-0004 | UPS | ITPS6.1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-05-2022 | 08:05:53 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 06-02-2023 | 05:00:00 | 06-02-2023 | 05:30:00
L6-6H1-0003 | FCU | 6H1FCU | PLC board Failure |  | 10-01-2023 | 08:05:03 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 06-07-2022 | 08:00:00 | 06-07-2022 | 11:00:00
L6-6H1-0013 | FCU | 6H1FCU | The Motor Failure |  | 27-01-2023 | 08:05:13 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 06-10-2022 | 08:00:00 | 06-10-2022 | 11:00:00
L6-6E1-0006 | AHUS | 6E1AHUS | the AHU heater Failure |  | 25-12-2022 | 08:03:11 | Fire Alarm | 60 | the AHU heater Failure | Hardware | Yes | PHA_CJV_156 | fire fighting extingiushed the fire |  | 06-12-2021 | 22:30:00 | 06-12-2021 | 23:30
L6-6F1-0012 | ACID | 6F1ACID | SIL2 sensor activated |  | 19-01-2023 | 08:00:53 | TSY-SCADA System | 3 | SIL2 sensor activated | Software | No |  | Automatically rectified when the person closed the door |  | 06-12-2022 | 13:50:00 | 06-12-2022 | 13:53:00
L4-4C1-00010 | SFDS | 4C1SFDS | Sump Pump Panel having Feedback Contactor alarm SUP-4C1-BL-004 |  | 30-01-2023 | 08:00:37 | Alarm indicated in Scada/BMS System | 123 | Sump Pump Panel having Feedback Contactor alarm SUP-4C1-BL-004 | Hardware | No | N/A | Rasied PR for the troubleshooting of Panel |  | 06-12-2022 | 13:50:00 | 06-12-2022 | 15:53
L6-6D2-0024 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 04-01-2023 | 08:03:02 | during daily checking of UPS it was observed in (alarms Log) | 360 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 07-02-2022 | 09:00:00 | 07-02-2022 | 15:00:00
L6-6F1-0015 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 07-01-2023 | 08:03:44 | during daily checking of UPS it was observed in (alarms Log) | 2.0167 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 07-02-2022 | 07:58:00 | 07-02-2022 | 08:00:01
L4-4C1-00016 | AHUS | 4C1AHUS | AHU Filters showing dirty |  | 20-02-2023 | 08:00:43 | Alarm indicated in Scada/BMS System | 420 | AHU Filters showing dirty | Hardware | No | N/A | Cleaned the Filters |  | 07-02-2023 | 08:00:00 | 07-02-2023 | 15:00:00
L4-4B1-00001 | FCU | 4B1FCU | PCB not working (red color) |  | 04-02-2023 | 08:00:01 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | Required Configuration | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 07-02-2023 | 16:40:00 | 07-02-2023 | 17:40:00
L4-4B1-00011 | FCU | 4B1FCU | FCU Filters showing dirty |  | 26-02-2023 | 08:00:11 | Alarm idicated from SCADA/BMS System | 120 | FCU Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 07-02-2023 | 16:40:00 | 07-02-2023 | 18:40
L4-4E1-00022 | FCU | 4E1FCU | Dirty Filter |  | 14-09-2022 | 08:01:39 | Found alarm in BMS, lead to inspection of failure identification | 180 | Dirty Filter | Hardware | No | N/A | Assigned care taking team to clean |  | 07-02-2023 | 08:00:00 | 07-02-2023 | 11:00:00
L6-6G2-0023 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-08-2022 | 08:04:51 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 07-02-2023 | 13:00:00 | 07-02-2023 | 17:00:00
L4-4C1-00024 | FCU | 4C1FCU | FCU Filters showing dirty - FCU-4C1-GL-029 |  | 21-11-2022 | 08:00:51 | Alarm indicated in Scada/BMS System | 180 | FCU Filters showing dirty - FCU-4C1-GL-029 | Hardware | No | N/A | Instructed team to clea n the filters |  | 07-03-2023 | 13:00:00 | 07-03-2023 | 16:00:00
L6-6H1-0025 | ACID | 6H1ACID | SIL2 sensor activated |  | 28-01-2023 | 08:00:55 | TSY-SCADA System | 1 | SIL2 sensor activated | Software | No |  | Automatically rectified |  | 07-12-2022 | 09:29:00 | 07-12-2022 | 09:30:00
L4-4D1-00001 | FDS | 4D1FDS | Isolator Module Damaged MFACP-4D1-Cl-02 |  | 15-01-2023 | 08:00:57 | Found during Physical Inspection | 180 | Isolator Module Damaged MFACP-4D1-Cl-02 | Hardware | No | N/A | Replaced Isolator Module |  | 08-01-2023 | 08:00:00 | 08-01-2023 | 11:00:00
L6-6E1-0012 | UPS | 6E1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 10-01-2023 | 08:03:17 | during daily checking of UPS it was observed in (alarms Log) | 420 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 08-02-2022 | 08:00:00 | 08-02-2022 | 15:00:00
L6-6F1-0016 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-01-2023 | 08:03:45 | during daily checking of UPS it was observed in (alarms Log) | 62.0333 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 08-02-2022 | 08:58:00 | 08-02-2022 | 10:00
L4-4C2-00007 | ACID | 4C2ACID | Termination work incomplete MAT-GL-110 |  | 11-03-2023 | 08:00:06 | BMS and SCADA alarms. | 240 | Termination work incomplete MAT-GL-110 | Hardware | No | N/A | Informed ICT team to rectify |  | 08-02-2023 | 08:00:00 | 08-02-2023 | 12:00:00
L4-4E1-00021 | ACID | 4E1ACID | Acid door access have no power but still appearing online in ACID system |  | 26-09-2022 | 08:00:31 | Physical inspection lead to the failure identification | 420 | Acid door access have no power but still appearing online in ACID system | Software | No | N/A | Informed ICT team to rectify |  | 08-02-2023 | 08:00:00 | 08-02-2023 | 15:00:00
L4-4B1-00002 | FCU | 4B1FCU | Tranformer burned |  | 28-02-2023 | 08:00:02 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | ACID doors are offline | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 08-02-2023 | 17:40:00 | 08-02-2023 | 18:40:00
L6-6G2-0024 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 12-01-2023 | 08:04:52 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 08-02-2023 | 14:00:00 | 08-02-2023 | 18:00:00
L6-6G1-0001 | FPUMP (BUILD) | 4G1FPUMP (BUILD) | the Imperller Failure |  | 16-01-2023 | 08:03:56 | during T&C found the pump not raise the pressure and overheating | 180 | the Imperller Failure | Hardware | No | N/A | replace the Imperller of the Jockey pump |  | 08-03-2022 | 08:00:00 | 08-03-2022 | 11:00:00
L4-4C1-00025 | AHUS | 4C1AHUS | AHU Filters showing dirty -AHU-4C1-CL-003 |  | 21-11-2022 | 08:00:52 | Alarm indicated in Scada/BMS System | 180 | AHU Filters showing dirty -AHU-4C1-CL-003 | Hardware | No | N/A | Instructed team to clea n the filters |  | 08-03-2023 | 13:00:00 | 08-03-2023 | 16:00:00
L4-4E1-00028 | CPM | 4E1CPM | CWP working in VFD mode - CPM-4E1-CL-02 |  | 04-01-2023 | 08:01:45 | Physical inspection lead to the failure identification | 90 | CWP working in VFD mode - CPM-4E1-CL-02 | Software | No | N/A | Informed CPM supplier |  | 08-03-2023 | 11:30:00 | 08-03-2023 | 13:00:00
L6-6E1-0009 | FCU | 6E1FCU | The Motor Failure |  | 15-01-2023 | 08:03:14 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 08-08-2022 | 09:00:00 | 08-08-2022 | 12:00:00
L6-6H1-0014 | FCU | 6H1FCU | The Motor Failure |  | 28-01-2023 | 08:05:14 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 08-10-2022 | 08:00:00 | 08-10-2022 | 11:00:00
L6-6D2-0013 | CCTV | 6D2CCTV | ICT-LAN port was enabled by ICT engineer. Loss of SCADA-ISM Connectivity to be investigated and checked in parallel. The issue happened after restoring the SCADA-ISM Connectivity |  | 25-08-2022 | 08:00:25 | TSY-SCADA System | 50 | ICT-LAN port was enabled by ICT engineer. Loss of SCADA-ISM Connectivity to be investigated and checked in parallel. The issue happened after restoring the SCADA-ISM Connectivity | Hardware | No |  | we disable the port which is spare port, then we establish the network connectivity and everything become normal. |  | 08-12-2022 | 08:25:00 | 08-12-2022 | 09:15:00
L6-6D2-0012 | INTERCOM | 6D2INTERCOM | all 6D2 intercom failure. ICT-LAN port was enabled by ICT engineer. Loss of SCADA-ISM Connectivity to be investigated and checked in parallel. The issue happened after restoring the SCADA-ISM Connectivity |  | 20-08-2022 | 08:00:46 | TSY-SCADA System | 50 | all 6D2 intercom failure. ICT-LAN port was enabled by ICT engineer. Loss of SCADA-ISM Connectivity to be investigated and checked in parallel. The issue happened after restoring the SCADA-ISM Connectivity | Hardware | No |  | we disable the port which is spare port, then we establish the network connectivity and everything become normal. |  | 08-12-2022 | 08:25:00 | 08-12-2022 | 09:15:00
L4-4G1-00018 | LCS | 4G1LCS | LCP-4G1-PL-01 Lighting Relay status set to off due to panel termination ongoing |  | 02-10-2022 | 08:02:23 | Monitoring from SCADA/ BMSstem | 65 | LCP-4G1-PL-01 Lighting Relay status set to off due to panel termination ongoing | Hardware | No | N/A | Informed to BMS team |  | 08-12-2022 | 08:25:00 | 08-12-2022 | 09:30:00
L4-4C1-000022 | MCC | 4C1MCC | Power not available from MCC panel |  | 12-01-2022 | 08:00:49 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 107 | Power not available from MCC panel | Hardware | No | N/A | Informed Electrical team to rectify |  | 08-12-2022 | 08:25:00 | 08-12-2022 | 10:12:00
L4-4G1-00032 | MCC | 4G1MCC | and 4G1-MCCIPL-01 BMS RECTIFICATION ON LCS |  | 16-06-2022 | 08:02:37 | Monitoring from SCADA/bms System | 80 | and 4G1-MCCIPL-01 BMS RECTIFICATION ON LCS | Software | No | N/A | Informed BMS team to rectify |  | 08-12-2022 | 08:25:00 | 08-12-2022 | 09:45:00
L6-6G1-0018 | PDP | 6G1PDP | MCB Breaker Failure |  | 18-02-2023 | 08:04:13 | Physical inspection lead to the failure identification | 420 | MCB Breaker Failure | Hardware | No | N/A | check the panel and termination then replace the breaker |  | 09-01-2023 | 05:00:00 | 09-01-2023 | 12:00:00
L6-6D2-0019 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 16-10-2022 | 08:02:57 | during daily checking of UPS it was observed in (alarms Log) | 120 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 09-02-2022 | 17:00:00 | 09-02-2022 | 19:00:00
L6-6F1-0017 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2023 | 08:03:46 | during daily checking of UPS it was observed in (alarms Log) | 2.05 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 09-02-2022 | 09:58:00 | 09-02-2022 | 10:00
L4-4C1-00020 | AHUS | 4C1AHUS | abnormal sound from motor |  | 09-10-2022 | 08:00:47 | Physical inspection lead to the failure identification | 300 | abnormal sound from motor | Hardware | No | N/A | Raised PR and invite supplier to repair |  | 09-02-2023 | 10:00:00 | 09-02-2023 | 15:00:00
L4-4B1-00003 | FCU | 4B1FCU | PCB not working & ON/OFF swicth not working |  | 01-02-2023 | 08:00:03 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | Programming Issue | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 09-02-2023 | 18:40:00 | 09-02-2023 | 19:40:00
L6-6G2-0025 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 14-01-2023 | 08:04:53 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 09-02-2023 | 15:00:00 | 09-02-2023 | 19:00:00
L4-4C1-00004 | FCU | 4C1FCU | FCU not running due to contactor problem |  | 01-02-2023 | 08:00:31 | Alarm in BMS system, lead to physical inspection of failure indentification | 70 | FCU not running due to contactor problem | Hardware | No | N/A | Informed to BMS team to check and rectify |  | 09-03-2023 | 13:00:00 | 09-03-2023 | 14:10:00
L4-4C1-00026 | FCU | 4C1FCU | FCU Filters showing dirty -FCU-4C1-CL-036 |  | 24-11-2022 | 08:00:53 | Alarm indicated in Scada/BMS System | 180 | FCU Filters showing dirty -FCU-4C1-CL-036 | Hardware | No | N/A | Instructed team to clea n the filters |  | 09-03-2023 | 13:00:00 | 09-03-2023 | 16:00:00
L4-4E1-00025 | ACID | 4E1ACID | Not working with access card AC-4E1-CL-10 |  | 29-12-2022 | 08:00:32 | Physical inspection lead to the failure identification | 180 | Not working with access card AC-4E1-CL-10 | Software | No | N/A | Informed ICT team to rectify |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L4-4E1-00034 | ACID | 4E1ACID | Not working with access card - AC-4E1-CL-07 - AC-4E1-CL-102 |  | 13-02-2023 | 08:00:34 | Physical inspection lead to the failure identification | 180 | Not working with access card - AC-4E1-CL-07 - AC-4E1-CL-102 | Software | No | N/A | Informed ICT team to rectify |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L4-4D1-00009 | CCTV | 4D1CCTV | 08 CCTV Camera's are Offline and 02 CCTV Camera's required to configure by ICT team CM-PL008, CM-PL010, CM-PL013, CM-PL015, CMIN-GL009, CMIN-PL107, CFIX-CL110, CMIN-GL007, CMIP-CL012 |  | 25-02-2023 | 08:00:14 | Found in SCADA Alarms | 180 | 08 CCTV Camera's are Offline and 02 CCTV Camera's required to configure by ICT team CM-PL008, CM-PL010, CM-PL013, CM-PL015, CMIN-GL009, CMIN-PL107, CFIX-CL110, CMIN-GL007, CMIP-CL012 | Software | No | N/A | CCTV (CM-PL008,CM-PL010,CM-PL013,CM-PL015, CMIN-PL107,CMIN-GL009) are rectified by ICT team, and ICT team informed for the remaining CCTV rectification |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L4-4D1-00020 | CWS | 4D1CWS | Chilled water pump is not working on time schedule from CPM, working continously CHP-4D1-CL-002 CHP-4D1-CL-003 CHP-4D1-CL-004 CHP-4D1-CL-005 CHP-4D1-CL-006 |  | 21-02-2023 | 08:01:16 | Physical inspection lead to the failure identification | 180 | Chilled water pump is not working on time schedule from CPM, working continously CHP-4D1-CL-002 CHP-4D1-CL-003 CHP-4D1-CL-004 CHP-4D1-CL-005 CHP-4D1-CL-006 | Software | No | N/A | Informed to CPM supplier |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L6-6F1-0005 | CWS | 6F1CWS | the bearing Failure |  | 04-02-2023 | 08:03:34 | overheat and noise of pump | 180 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L6-6F1-0006 | CWS | 6F1CWS | the bearing Failure |  | 08-03-2022 | 08:03:35 | overheat and noise of pump | 180 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L6-6F1-0007 | CWS | 6F1CWS | the bearing Failure |  | 01-12-2022 | 08:03:36 | overheat and noise of pump | 180 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L6-6F1-0008 | CWS | 6F1CWS | the bearing Failure |  | 10-08-2022 | 08:03:37 | overheat and noise of pump | 180 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L6-6G2-0017 | MCC | 6G2MCC | MCC breaker Failure |  | 25-01-2023 | 08:04:45 | Physical inspection lead to the failure identification | 180 | MCC breaker Failure | Hardware | No | N/A | Reported to our specialist supplier (META) |  | 09-10-2022 | 08:00:00 | 09-10-2022 | 11:00:00
L4-4E1-00003 | LIFT | 4E1LIFT | Red color appear on border of Lifts system in Scada Lift 2,3,5,6,7,8 |  | 28-02-2023 | 08:00:51 | Found alarm in Scada, lead to inspection of failure identification | 120 | Red color appear on border of Lifts system in Scada Lift 2,3,5,6,7,8 | Software | No | N/A | Informed OTIS team to rectify |  | 10-01-2023 | 09:00:00 | 10-01-2023 | 11:00:00
L6-6F1-0018 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 16-02-2023 | 08:03:47 | during daily checking of UPS it was observed in (alarms Log) | 2.0667 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 10-02-2022 | 10:58:00 | 10-02-2022 | 11:00
L4-4B1-00004 | FCU | 4B1FCU | FCU coil Leakage |  | 25-02-2023 | 08:00:04 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | Programming Issue | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 10-02-2023 | 19:40:00 | 10-02-2023 | 20:40:00
L6-6G2-0030 | GEN | 6G2GEN | Generator lights burned |  | 25-01-2023 | 08:04:58 | during daily cartaking activites | 420 | Generator lights burned | Hardware | No | N/A | change the lights with new termination and good dressing of wiring |  | 10-02-2023 | 08:00:00 | 10-02-2023 | 15:00:00
L4-4C2-00003 | LDP | 4C2LDP | SCADA Program Update Require |  | 26-02-2023 | 08:01:57 | BMS and SCADA alarms. | 77 | SCADA Program Update Require | Software | No | N/A | To be check with SCADA team to update |  | 10-02-2023 | 06:58:00 | 10-02-2023 | 08:15:00
L4-4B1-00012 | MCC | 4B1MCC | Transformer Burn by over load |  | 19-01-2023 | 08:00:12 | Monitoring from BMS System | 482 | Transformer Burn by over load | Hardware | No | N/A | Rectify by site team |  | 10-02-2023 | 06:58:00 | 10-02-2023 | 15:00:00
L4-4B1-00013 | MCC | 4B1MCC | Transformer Burn by over load |  | 19-02-2023 | 08:00:13 | Monitoring from BMS System | 246 | Transformer Burn by over load | Hardware | No | N/A | Rectify by site team |  | 10-02-2023 | 15:54:00 | 10-02-2023 | 20:00:00
L6-6G2-0026 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-01-2023 | 08:04:54 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 10-02-2023 | 16:00:00 | 10-02-2023 | 20:00:00
L4-4C1-00005 | DWS | 4C1DWS | Flush sensor not working in all 4 toilets FWC & MWC |  | 05-02-2023 | 08:00:32 | Physical inspection lead to the failure identification | 180 | Flush sensor not working in all 4 toilets FWC & MWC | Hardware | No | N/A | Raised PR and waiting for delivery |  | 10-03-2022 | 08:00:00 | 10-03-2022 | 11:00:00
L6-C&C6.4-0001 | MISTING | C&C6.1MISTING | The Zone valve Failure |  | 19-01-2023 | 08:05:58 | from control panel send command for open the valve but no rsponse | 180 | The Zone valve Failure | Hardware | No | N/A | Pcb card rectified |  | 10-03-2022 | 08:00:00 | 10-03-2022 | 11:00:00
L6-C&C6.4-0002 | MISTING | C&C6.1MISTING | The Zone valve Failure |  | 19-02-2023 | 08:05:59 | from control panel send command for open the valve but no rsponse | 180 | The Zone valve Failure | Hardware | No | N/A | replaced with new one |  | 10-03-2022 | 08:00:00 | 10-03-2022 | 11:00:00
L4-4B1-00019 | PFAN | 4B1PFAN | LPF Motor winding got damaged |  | 25-02-2023 | 08:00:19 | Alarm not indicated in scada/BMS system, lead to physical inspection of failure indentification | 540 | LPF Motor winding got damaged | Hardware | No | N/A | Sent motor to workshop for rewinding |  | 10-03-2023 | 08:00:00 | 10-03-2023 | 17:00:00
L6-6H1-0007 | FCU | 6H1FCU | PLC board Failure |  | 18-01-2023 | 08:05:07 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 10-08-2022 | 09:00:00 | 10-08-2022 | 12:00:00
L6-6H2-0002 | FPUMP (BUILD) | 6H2FPUMP (BUILD) | the pump motor Failure |  | 10-01-2023 | 08:05:39 | the pump motor burned | 180 | the pump motor Failure | Hardware | No | N/A | Rewind the pump motor |  | 10-08-2022 | 09:00:00 | 10-08-2022 | 12:00:00
L4-4G1-00015 | FCU | 4G1FCU | FCU-013 ,24,PCB board, power board & transformer damaged, need to replace |  | 01-06-2022 | 08:02:20 | Monitoring from SCADA/ BMS | 60 | FCU-013 ,24,PCB board, power board & transformer damaged, need to replace | Hardware | No | N/A | Waiting for material delivery |  | 10-11-2022 | 08:00:00 | 10-11-2022 | 09:00:00
L6-6G1-0014 | FCU | 6G1FCU | PLC & PCB board Failure |  | 31-01-2023 | 08:04:09 | The PCB & PCB board Burned | 180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 10-11-2022 | 08:00:00 | 10-11-2022 | 11:00:00
L4-4D1-00017 | ACID | 4D1ACID | ACID Doors Card Reader not working AC-4D1-CL-102, AC-4D1-CL-031 |  | 02-02-2023 | 08:00:04 | Found in ACID System | 60 | ACID Doors Card Reader not working AC-4D1-CL-102, AC-4D1-CL-031 | Software | No | N/A | Informed ICT team to Rectify Doors |  | 11-01-2022 | 08:00:00 | 11-01-2022 | 09:00:00
L6-6H1-0001 | AIC | 6H1AIC | the transformer Failure |  | 30-01-2023 | 08:05:01 | the transformer Burned | 180 | the transformer Failure | Hardware | No | N/A | replaced the transformer |  | 11-01-2022 | 08:00:00 | 11-01-2022 | 11:00:00
L6-6D2-0020 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 26-10-2022 | 08:02:58 | during daily checking of UPS it was observed in (alarms Log) | 120 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 11-02-2022 | 01:00:00 | 11-02-2022 | 03:00:00
L6-6F1-0019 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 07-01-2023 | 08:03:48 | during daily checking of UPS it was observed in (alarms Log) | 62.0833 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 11-02-2022 | 11:18 | 11-02-2022 | 12:20
L4-4B1-00005 | FCU | 4B1FCU | PCB not working (red & Green color) |  | 02-02-2023 | 08:00:05 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | Programming Issue | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 11-02-2023 | 20:40:00 | 11-02-2023 | 21:40:00
L4-4C1-00017 | FCU | 4C1FCU | FCU Filters showing dirty |  | 27-02-2023 | 08:00:44 | Alarm indicated in Scada/BMS System | 60 | FCU Filters showing dirty | Hardware | No | N/A | Instructed team to clea n the filters |  | 11-02-2023 | 10:00:00 | 11-02-2023 | 11:00:00
L6-6G2-0027 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-01-2023 | 08:04:55 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 11-02-2023 | 17:00:00 | 11-02-2023 | 21:00:00
L4-4D1-00003 | CWS | 4D1CWS | Pressurizing Unit Damaged |  | 10-01-2023 | 08:00:59 | Found during Physical Inspection | 210 | Pressurizing Unit Damaged | Hardware | No | N/A | PU Replaced |  | 11-03-2023 | 08:00:00 | 11-03-2023 | 11:30:00
L6-6H1-0004 | FCU | 6H1FCU | PLC board Failure |  | 11-01-2023 | 08:05:04 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 11-07-2022 | 08:00:00 | 11-07-2022 | 11:00:00
L6-6D2-0011 | FM200 | 6D2FM200 | the manual release botton Failure |  | 10-08-2022 | 08:02:49 | FM200 room alarm, fond the gas discharged | 180 | the manual release botton Failure | Hardware | No | N/A | recharge the cylinders by NAFFCO |  | 11-10-2022 | 09:00:00 | 11-10-2022 | 12:00:00
L4-4C1-00028 | CCTV | 4C1CCTV | 3 cameras need configuration CMIN-GL003 CMIN-CL110 |  | 24-11-2022 | 08:00:12 | Alarm indicated in Scada/ISM System | 120 | 3 cameras need configuration CMIN-GL003 CMIN-CL110 | Software | No | N/A | Informed ICT team to do reconfiguration of CCTV |  | 12-01-2022 | 09:00:00 | 12-01-2022 | 11:00:00
L6-6E1-0007 | SEXF | 6E1SEXF | FAN MOTOR Failure |  | 18-12-2022 | 08:03:12 | The Motor Burned | 180 | FAN MOTOR Failure | Hardware | No | N/A | rewind the motor |  | 12-01-2022 | 09:00:00 | 12-01-2022 | 12:00:00
L6-6F1-0020 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 07-01-2023 | 08:03:49 | during daily checking of UPS it was observed in (alarms Log) | 302.1 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 12-02-2022 | 2:58 | 12-02-2022 | 8:00
L4-4B1-00006 | FCU | 4B1FCU | PCB not working (red color) |  | 02-05-2023 | 08:00:06 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | Hard ware issue | Hardware | No | N/A | PR raise and waiting for supplier to deliver |  | 12-02-2023 | 21:40:00 | 12-02-2023 | 22:40:00
L4-4C2-00005 | GEN | 4D1GEN | Battery discharged due to unfunctional charger |  | 08-03-2023 | 08:01:59 | BMS and SCADA alarms. | 300 | Battery discharged due to unfunctional charger | Hardware | No | N/A | Generator supplier to replace battery charger |  | 12-02-2023 | 08:00:00 | 12-02-2023 | 13:00:00
L4-4C1-00006 | INTERCOM | 4C1INTERCOM | Intercom not working |  | 14-02-2023 | 08:00:42 | Alarm indicated in Scada/Acid System | 30 | Intercom not working | Software | No | N/A | Informed ICT team to retify communication issue for intercom |  | 12-02-2023 | 09:00:00 | 12-02-2023 | 09:30:00
L6-6G2-0028 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 21-01-2023 | 08:04:56 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 12-02-2023 | 18:00:00 | 12-02-2023 | 22:00:00
L4-4C1-00027 | ACID | 4C1ACID | Door not opening with card L4C1_ACGL003 |  | 24-11-2022 | 08:00:26 | Alarm not indicated in scada/ACID system, lead to physical inspection of failure indentification | 60 | Door not opening with card L4C1_ACGL003 | Software | No | N/A | Instructed ICT to rectify the issue |  | 12-09-2021 | 09:00:00 | 12-09-2021 | 10:00:00
L4-4D1-00016 | ACID | 4D1ACID | ACID Doors Lock Hardware Issue AC-4D1-GL-102, AC-4D1-BL-004, AC-4D1-GL-002, AC-4D1-GL-005 |  | 01-02-2023 | 08:00:28 | Found during Physical Inspection | 60 | ACID Doors Lock Hardware Issue AC-4D1-GL-102, AC-4D1-BL-004, AC-4D1-GL-002, AC-4D1-GL-005 | Hardware | No | N/A | Informed Archi team to Rectify Doors |  | 12-09-2021 | 09:00:00 | 12-09-2021 | 10:00:00
L4-4D1-00004 | DWS | 4D1DWS | Automatic Flash Valve Piston damaged EWC-4D1-CL-02,03,04 |  | 29-07-2021 | 08:01:00 | Found during Physical Inspection | 60 | Automatic Flash Valve Piston damaged EWC-4D1-CL-02,03,04 | Hardware | No | N/A | Waiting for material Delivery |  | 12-09-2021 | 09:00:00 | 12-09-2021 | 10:00:00
L6-6G1-0007 | FCU | 6G1FCU | PLC & PCB board Failure |  | 14-01-2023 | 08:04:02 | The PCB & PCB board Burned | 180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 12-10-2022 | 08:00:00 | 12-10-2022 | 11:00:00
L6-6G2-0014 | FCU | 6G2FCU | The Motor Failure |  | 12-01-2023 | 08:04:42 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 12-10-2022 | 08:00:00 | 12-10-2022 | 11:00:00
L6-6F1-0011 | FCU | 6F1FCU | The Transformer Failure |  | 31-01-2023 | 08:03:40 | The Transformer Burned | 60 | The Transformer Failure | Hardware | No | N/A | reported by supplier and need to replace transformer |  | 12-11-2022 | 08:00:00 | 12-11-2022 | 09:00:00
L6-6G1-0015 | FCU | 6G1FCU | PLC board Failure |  | 09-01-2023 | 08:04:10 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 12-11-2022 | 08:00:00 | 12-11-2022 | 11:00:00
L4-4G1-00001 | LDP | ES26LDP | MONITOR GENERAL FAULT (TMCS-Command issue) |  | 11-03-2023 | 08:02:06 | found in SCADA / TMCS PANEL | 420 | MONITOR GENERAL FAULT (TMCS-Command issue) | Software | No | N/A | Informed TMCS |  | 13-01-2023 | 09:00:00 | 13-01-2023 | 16:00:00
L6-6F1-0021 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 05-02-2023 | 08:03:50 | during daily checking of UPS it was observed in (alarms Log) | 1 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 13-02-2022 | 13:08 | 13-02-2022 | 13:09
L4-4G1-00027 | ACID | 4G1ACID | ( L4G1-MGC-CL-11 L4G1-MAT-GL-100-102 - this 3 door open for access) ( Aall this door repair done L4G1-AC-PL-15-1-11 L4G1-AC-PL-03, L4G1-AC-GL-09 -10- L4G1-AC-CL-23-22-21-26-21 ) |  | 05-11-2022 | 08:00:07 | Monitoring from SCADA/ACID System | 420 | ( L4G1-MGC-CL-11 L4G1-MAT-GL-100-102 - this 3 door open for access) ( Aall this door repair done L4G1-AC-PL-15-1-11 L4G1-AC-PL-03, L4G1-AC-GL-09 -10- L4G1-AC-CL-23-22-21-26-21 ) | Hardware | No | N/A | informed ICT TEAM |  | 13-02-2023 | 07:00:00 | 13-02-2023 | 14:00:00
L4-4C1-00018 | CCTV | 4C1CCTV | 2 cameras are offline and 2 cameras need configuration -CMIN-PL-011 CFIX-CL-110 CMIN-GL-005 |  | 09-10-2022 | 08:00:10 | Alarm indicated in Scada/ISM System | 60 | 2 cameras are offline and 2 cameras need configuration -CMIN-PL-011 CFIX-CL-110 CMIN-GL-005 | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV |  | 13-02-2023 | 08:00:00 | 13-02-2023 | 09:00:00
L4-4B1-00015 | FAN | 4B1FAN | SAF Filters showing dirty |  | 06-12-2021 | 08:00:15 | Alarm idicated from SCADA/BMS System | 62 | SAF Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 13-02-2023 | 06:58:00 | 13-02-2023 | 08:00:00
L4-4B1-00007 | FCU | 4B1FCU | FCU Motor winding got damaged due to wrong termination |  | 04-02-2023 | 08:00:07 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | FCU Motor winding got damaged due to wrong termination | Hardware | No | N/A | PR raise and waiting for supplier to repair |  | 13-02-2023 | 22:40:00 | 13-02-2023 | 23:40
L4-4B1-00016 | FCU | 4B1FCU | FCU Filters showing dirty |  | 19-02-2023 | 08:00:16 | alarm idicated from SCADA/BMS System | 122 | FCU Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 13-02-2023 | 06:58:00 | 13-02-2023 | 09:00:00
L4-4C1-00008 | GEN | 4C1GEN | Generator having alarm of Engine oil low level |  | 28-02-2023 | 08:00:35 | Alarm indicated in Scada/BMS System | 120 | Generator having alarm of Engine oil low level | Hardware | No | N/A | Raised PR for the maintenance of generator. |  | 13-02-2023 | 17:00:00 | 13-02-2023 | 19:00:00
L4-4C2-00008 | GEN | 4C2GEN | Alarm for Oil level |  | 26-01-2023 | 08:02:02 | BMS and SCADA alarms. | 180 | Alarm for Oil level | Hardware | No | N/A | Generator supplier to replace oil and filters |  | 13-02-2023 | 08:00:00 | 13-02-2023 | 11:00:00
L6-6E1-0011 | PFC | 6E1PFC | the PFC Failure |  | 15-02-2023 | 08:03:16 | Physical inspection lead to the failure identification | 62 | the PFC Failure | Hardware | No | N/A | Requested from specialist supplier (META) |  | 13-02-2023 | 06:58:00 | 13-02-2023 | 08:00:00
L6-6G2-0029 | UPS | 6G2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 22-01-2023 | 08:04:57 | during daily checking of UPS it was observed in (alarms Log) | 240 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 13-02-2023 | 19:00:00 | 13-02-2023 | 23:00:00
L6-6H1-0005 | FCU | 6H1FCU | PLC board Failure |  | 14-01-2023 | 08:05:05 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 13-07-2022 | 08:00:00 | 13-07-2022 | 11:00:00
L4-4G1-00003 | FDS | 4G1FDS | CT1 device for MSFD status |  | 30-01-2023 | 08:02:08 | Monitoring from SCADA/ Fire Alarm PANEL | 360 | CT1 device for MSFD status | Hardware | No | N/A | Replaced CT1 DEVICE |  | 14-01-2023 | 08:00:00 | 14-01-2023 | 14:00:00
L4-4G1-00002 | LDP | 4G1LDP | MONITOR GENERAL FAULT (TMCS-Command issue) |  | 30-01-2023 | 08:02:07 | found in SCADA / TMCS PANEL | 180 | MONITOR GENERAL FAULT (TMCS-Command issue) | Software | No | N/A | Informed TMCS |  | 14-01-2023 | 10:00:00 | 14-01-2023 | 13:00:00
L6-6F1-0022 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 02-02-2023 | 08:03:51 | during daily checking of UPS it was observed in (alarms Log) | 182.1333 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 14-02-2022 | 14:58:00 | 14-02-2022 | 18:00
L4-4E1-00016 | ACID | 4E1ACID | Acid doors are offline - L4E1-ACCL12, - L4E1-ACCL18 |  | 26-09-2021 | 08:00:29 | Found alarm in Scada, lead to inspection of failure identification | 420 | Acid doors are offline - L4E1-ACCL12, - L4E1-ACCL18 | Software | No | N/A | Informed ICT team to rectify |  | 14-02-2023 | 08:00:00 | 14-02-2023 | 15:00:00
L4-4E1-00017 | CBS | 4E1CBS | Programming issue |  | 27-04-2021 | 08:01:34 | Found alarm in BMS, lead to inspection of failure identification | 180 | Programming issue | Software | No | N/A | Informed Elec team to rectify |  | 14-02-2023 | 10:00:00 | 14-02-2023 | 13:00:00
L4-4B1-00017 | FCU | 4B1FCU | FCU Filters showing dirty |  | 26-02-2023 | 08:00:17 | Alarm idicated from SCADA/BMS System | 60 | FCU Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 14-02-2023 | 09:00:00 | 14-02-2023 | 10:00:00
L4-4E1-00036 | CWS | 4E1CWS | Chilled water pump is not working on time schedule from CPM, working continously CHP-4E1-CL-002 CHP-4E1-CL-003 CHP-4E1-CL-004 CHP-4E1-CL-005 CHP-4E1-CL-006 |  | 21-02-2023 | 08:01:53 | Physical inspection lead to the failure identification | 60 | Chilled water pump is not working on time schedule from CPM, working continously CHP-4E1-CL-002 CHP-4E1-CL-003 CHP-4E1-CL-004 CHP-4E1-CL-005 CHP-4E1-CL-006 | Software | No | N/A | Informed to CPM supplier |  | 14-09-2022 | 08:00:00 | 14-09-2022 | 09:00:00
L4-4G1-00005 | MISTING | 4G1MISTING | Device OFF |  | 30-01-2023 | 08:02:10 | Monitoring from SCADA/ CHECKED ON FIELD SIDE | 30 | Device OFF | Software | No | N/A | Panel turned on mannually |  | 15-01-2023 | 07:00:00 | 15-01-2023 | 07:30:00
L6-6H1-0027 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2023 | 08:05:27 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 15-01-2023 | 07:00:00 | 15-01-2023 | 07:30:00
L6-6F1-0023 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 19-01-2023 | 08:03:52 | during daily checking of UPS it was observed in (alarms Log) | 15.15 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 15-02-2022 | 15:15 | 15-02-2022 | 15:30
L4-4B1-00010 | CCTV | 4B1CCTV | 8 CCTV Camera are not working 4 CCTV's are offline & 3 CCTV's need to configured by ICT Team) - L4B1-CMIN-CL-007 L4B1-CMIN-CL-019 L4B1-CMIN-CL-121 L4B1-CMIP-CL-001 L4B1-CMIN-BLU-002 L4B1-CFIX-CL010 L4B1-CFIX-CL101 |  | 07-02-2023 | 08:00:08 | Monitoring from SCADA/ISM System | 60 | 8 CCTV Camera are not working 4 CCTV's are offline & 3 CCTV's need to configured by ICT Team) - L4B1-CMIN-CL-007 L4B1-CMIN-CL-019 L4B1-CMIN-CL-121 L4B1-CMIP-CL-001 L4B1-CMIN-BLU-002 L4B1-CFIX-CL010 L4B1-CFIX-CL101 | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration og CCTV |  | 15-09-2022 | 09:00:00 | 15-09-2022 | 10:00:00
L6-6D2-0010 | CWS | 6D2CWS | the bearing Failure |  | 18-07-2022 | 08:02:48 | overheat and noise of pump | 180 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 15-09-2022 | 09:00:00 | 15-09-2022 | 12:00:00
L6-6E1-0013 | ACID | 6E1ACID | SIL2 sensor activated |  | 19-01-2023 | 08:00:52 | TSY-SCADA System | 180 | SIL2 sensor activated | Software | No |  | Automatically rectified when the person closed the door |  | 16-01-2023 | 20:11:00 | 16-01-2023 | 23:11:00
L4-4G1-00024 | SFDS | 4G1SFDS | Sump pump motor damaged |  | 29-10-2022 | 08:02:29 | Found during physical inspection | 21 | Sump pump motor damaged | Hardware | No | N/A | Waiting for material delivery |  | 16-01-2023 | 20:11 | 16-01-2023 | 20:32
L6-6H1-0028 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 04-05-2022 | 08:05:28 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 16-01-2023 | 08:00:00 | 16-01-2023 | 08:30:00
L6-6F1-0024 | UPS | 6F1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 05-01-2023 | 08:03:53 | during daily checking of UPS it was observed in (alarms Log) | 10.1667 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 16-02-2022 | 16:40 | 16-02-2022 | 16:50
L6-6G2-0005 | DWS | 6G2DWS | The Shaft Seal Failure |  | 25-01-2022 | 08:04:33 | Found leakage | 60 | The Shaft Seal Failure | Hardware | No | N/A | SHAFT SEAL replaced |  | 16-05-2022 | 09:00:00 | 2022-05-16 | 10:00
L6-6G1-0002 | FCU | 6G1FCU | The Motor Failure |  | 27-02-2023 | 08:03:57 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 16-08-2022 | 09:00:00 | 16-08-2022 | 12:00:00
L6-6H1-0015 | FCU | 6H1FCU | The Transformer Failure |  | 30-01-2023 | 08:05:15 | The Transformer Burned | 180 | The Transformer Failure | Hardware | No | N/A | Transformer replaced |  | 16-10-2022 | 08:00:00 | 16-10-2022 | 11:00:00
L6-6H1-0029 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 10-01-2023 | 08:05:29 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 17-01-2023 | 09:00:00 | 17-01-2023 | 09:30:00
L6-6G1-0019 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 21-02-2023 | 08:04:14 | during daily checking of UPS it was observed in (alarms Log) | 70.1833 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 17-02-2022 | 17:10 | 17-02-2022 | 18:20
L4-4G1-00016 | FCU | 4G1FCU | FCU-027, FCU blower damaged need to replace blower |  | 21-11-2022 | 08:02:21 | Monitoring from SCADA/ BMS | 120 | FCU-027, FCU blower damaged need to replace blower | Hardware | No | N/A | Waiting for material delivery |  | 17-08-2021 | 08:00:00 | 17-08-2021 | 10:00:00
L6-6E1-0004 | FCU | 6E1FCU | The Motor Failure |  | 24-12-2022 | 08:03:09 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 17-08-2021 | 08:00:00 | 17-08-2021 | 11:00:00
L6-6D2-0007 | FCU | 6D2FCU | The Motor Failure |  | 06-07-2022 | 08:02:45 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 17-11-2021 | 08:00:00 | 17-11-2021 | 11:00:00
L6-6D2-0008 | FCU | 6D2FCU | The Motor Failure |  | 11-07-2022 | 08:02:46 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 17-11-2021 | 08:00:00 | 17-11-2021 | 11:00:00
L4-4G1-00004 | FDS | 4G1FDS | Manual Call Point damged due to rain |  | 30-01-2023 | 08:02:09 | Monitoring from SCADA/ Fire Alarm PANEL | 360 | Manual Call Point damged due to rain | Hardware | No | N/A | Replaced MCP |  | 18-01-2023 | 08:00:00 | 18-01-2023 | 14:00:00
L4-4D1-00002 | GEN | 4D1GEN | Normal Power OFF |  | 17-01-2023 | 08:00:58 | Found during Physical Inspection | 9 | Normal Power OFF | Hardware | No | N/A | TSY Rectified the Panel and Now Normal Power is ON |  | 18-01-2023 | 14:30:00 | 18-01-2023 | 14:39
L6-6H1-0030 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 11-01-2023 | 08:05:30 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 18-01-2023 | 10:00:00 | 18-01-2023 | 10:30:00
L6-6G1-0020 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 23-02-2023 | 08:04:15 | during daily checking of UPS it was observed in (alarms Log) | 78.2 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 18-02-2022 | 18:08 | 18-02-2022 | 19:26
L4-4E1-00018 | ACID | 4E1ACID | Not working with access card - AC-4E1-CL-102 |  | 19-05-2021 | 08:00:05 | Physical inspection lead to the failure identification | 300 | Not working with access card - AC-4E1-CL-102 | Software | No | N/A | Informed ICT team to rectify |  | 18-02-2023 | 09:00:00 | 18-02-2023 | 14:00:00
L4-4E1-00019 | ACID | 4E1ACID | Acid door is closed but still appearing as always open in the ACID system - AC-4E1-BLU-01 |  | 21-01-2022 | 08:00:30 | Found alarm in ACID, lead to inspection of failure identification | 240 | Acid door is closed but still appearing as always open in the ACID system - AC-4E1-BLU-01 | Software | No | N/A | Informed ICT team to rectify |  | 18-02-2023 | 10:00:00 | 18-02-2023 | 14:00:00
L4-4B1-00018 | AHUS | 4B1AHUS | AHU Filters showing dirty |  | 11-01-2022 | 08:00:18 | Alarm idicated from SCADA/BMS System | 120 | AHU Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 18-02-2023 | 09:00:00 | 18-02-2023 | 11:00:00
L4-4E1-00020 | CCTV | 4E1CCTV | CCTV is offline |  | 27-01-2022 | 08:00:18 | Found alarm in Scada, lead to inspection of failure identification | 540 | CCTV is offline | Software | No | N/A | Informed ICT team to rectify |  | 18-02-2023 | 07:00:00 | 18-02-2023 | 16:00:00
L4-4B1-00020 | FDS | 4B1FDS | Maintenace alart for Dirty |  | 24-12-2022 | 08:00:20 | Alarm idicated from SCADA/BMS System | 10 | Maintenace alart for Dirty | Hardware | No | N/A | ELECTRICAL TEAM |  | 18-02-2023 | 17:00:00 | 18-02-2023 | 17:10
L4-4G1-00029 | GEN | 4G1GEN | GEN-4G1-CL-001 & 002 Minor Alarm set to fault _Communication issue for BMS |  | 12-11-2022 | 08:02:34 | Monitoring from SCADA/ BMS system | 60 | GEN-4G1-CL-001 & 002 Minor Alarm set to fault _Communication issue for BMS | Hardware | No | N/A | informed BMS |  | 18-02-2023 | 08:00:00 | 18-02-2023 | 09:00:00
L4-4G1-00025 | IS | 4G1IS | Irrigation pump motor damaged |  | 18-10-2022 | 08:02:30 | Found during physical inspection | 300 | Irrigation pump motor damaged | Hardware | No | N/A | Motor replaced |  | 18-02-2023 | 07:00:00 | 18-02-2023 | 12:00:00
L4-4D1-00005 | LDP | 4D1LDP | Luminair Failure Problem |  | 20-06-2021 | 08:01:01 | Found in BMS Alarms | 450 | Luminair Failure Problem | Hardware | No | N/A | Replaced damaged Lights and Rectified |  | 18-02-2023 | 08:00:00 | 18-02-2023 | 15:30:00
L6-6D2-0015 | LDP | 6D2LDP | all lighting connected to this module are not probably functinol |  | 01-10-2022 | 08:02:53 | Physical inspection lead to the failure identification | 60 | all lighting connected to this module are not probably functinol | Hardware | No | N/A | Requested from specialist supplier to change a module |  | 18-02-2023 | 08:00:00 | 18-02-2023 | 09:00:00
L4-4G1-00030 | MCC | 4G1MCC | MCC- Outgoing breaker fault to trips ,due to exf fan running full speed |  | 06-02-2022 | 08:02:35 | Monitoring from SCADA/ found on site | 120 | MCC- Outgoing breaker fault to trips ,due to exf fan running full speed | Hardware | No | N/A | Trip setting set to correct poit by ELECTRICAL TEAM |  | 18-02-2023 | 14:00:00 | 18-02-2023 | 16:00:00
L6-6G2-0032 | MCC | 6G2MCC | the bus bar burnt |  | 28-01-2023 | 08:05:00 | during daily cartaking activites, we found little smell | 39 | the bus bar burnt | Hardware | Yes | SRIL_CJV_005 | by supplier will rectified |  | 18-02-2023 | 08:00:00 | 18-02-2023 | 08:39:00
L6-6ITPS-0005 | VRF | ITPS6.1VRF | Thermostat screen damage |  | 17-11-2022 | 08:05:54 | during daily cartaking activites | 30 | Thermostat screen damage | Hardware | No | N/A | replaced the thermostat |  | 18-02-2023 | 10:00:00 | 18-02-2023 | 10:30:00
L6-6H1-0006 | FCU | 6H1FCU | PLC board Failure |  | 15-01-2023 | 08:05:06 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 18-07-2022 | 08:00:00 | 18-07-2022 | 11:00:00
L6-6G1-0011 | FCU | 6G1FCU | The Motor Failure |  | 29-05-2022 | 08:04:06 | The Motor Burned | 180 | The Motor Failure | Hardware | No | N/A | motor rewinding by supplier |  | 18-10-2022 | 08:00:00 | 18-10-2022 | 11:00:00
L6-6H1-0031 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 14-01-2023 | 08:05:31 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 19-01-2023 | 11:00:00 | 19-01-2023 | 11:30:00
L4-4D1-00019 | GEN | 4D1GEN | Day Tank Fuel Level Sensor not indicating fuel level in EVO panel |  | 21-02-2023 | 08:01:15 | Physical inspection lead to the failure identification | 71 | Day Tank Fuel Level Sensor not indicating fuel level in EVO panel | Software | No | N/A | Informed to supplier |  | 19-02-2022 | 16:49:00 | 19-02-2022 | 18:00:00
L6-6G1-0021 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 23-02-2023 | 08:04:16 | during daily checking of UPS it was observed in (alarms Log) | 50.2167 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 19-02-2022 | 19:10 | 19-02-2022 | 20:00
L6-6D2-0026 | AHUS | 6D2AHUS | Belt damaged |  | 08-01-2023 | 08:03:04 | during daily cartaking activites | 30 | Belt damaged | Hardware | No | N/A | replaced the belt |  | 19-02-2023 | 13:30:00 | 19-02-2023 | 14:00:00
L6-6F1-0025 | AHUS | 6F1AHUS | Air Filter Damaged |  | 30-11-2022 | 08:03:54 | during daily cartaking activites | 60 | Air Filter Damaged | Hardware | No | N/A | replaced Air filter |  | 19-02-2023 | 13:30:00 | 19-02-2023 | 14:30:00
L6-6E1-0022 | FCU | 6E1FCU | Duct heater switch broken |  | 07-02-2023 | 08:03:27 | during daily cartaking activites | 60 | Duct heater switch broken | Hardware | No | N/A | replaced the heater switch |  | 19-02-2023 | 14:30:00 | 19-02-2023 | 15:30:00
L4-4E1-00009 | AHUS | 4E1AHUS | Ahu not working in auto mode |  | 16-01-2023 | 08:01:26 | Physical inspection lead to the failure identification | 120 | Ahu not working in auto mode | Hardware | No | N/A | Informed Elec team |  | 20-01-2023 | 08:00:00 | 20-01-2023 | 10:00:00
L6-6H1-0032 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 15-01-2023 | 08:05:32 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 20-01-2023 | 12:00:00 | 20-01-2023 | 12:30:00
L6-6G1-0022 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 13-02-2023 | 08:04:17 | during daily checking of UPS it was observed in (alarms Log) | 60.2333 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 20-02-2022 | 20:00 | 20-02-2022 | 21:00
L4-4B1-00022 | AHUS | 4B1AHUS | AHU Filters showing dirty |  | 07-02-2023 | 08:00:22 | Alarm idicated from SCADA/BMS System | 840 | AHU Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 20-02-2023 | 03:00:00 | 20-02-2023 | 17:00:00
L6-6E1-0023 | CWS | 6E1CWS | the bearing Failure |  | 11-02-2023 | 08:03:28 | during daily cartaking activites overheat and noise of pump | 300 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 20-02-2023 | 10:00:00 | 20-02-2023 | 15:00:00
L4-4B1-00021 | FAN | 4B1FAN | SAF Filters showing dirty |  | 01-02-2023 | 08:00:21 | Alarm idicated from SCADA/BMS System | 360 | SAF Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 20-02-2023 | 09:00:00 | 20-02-2023 | 15:00:00
L6-6E1-0003 | CHILLER | 6E1CHILLER | The Chiller compressor Failure |  | 21-12-2022 | 08:03:08 | there was alarms and chiller/ MDB tripping many times | 180 | The Chiller compressor Failure | Hardware | No | N/A | Repairing chiller compressor |  | 20-06-2021 | 09:00:00 | 20-06-2021 | 12:00:00
L6-6H1-0033 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-01-2023 | 08:05:33 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 21-01-2023 | 13:00:00 | 21-01-2023 | 13:30:00
L6-6D2-0021 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 02-02-2023 | 08:02:59 | during daily checking of UPS it was observed in (alarms Log) | 60 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 21-02-2022 | 08:00:00 | 21-02-2022 | 09:00:00
L6-6G1-0023 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-02-2023 | 08:04:18 | during daily checking of UPS it was observed in (alarms Log) | 22.25 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 21-02-2022 | 21:58:00 | 21-02-2022 | 22:20
L6-6E1-0025 | CBS | 6E1CBS | the failure of F9A is not reflected on CBS |  | 31-10-2022 | 08:05:56 | Status monitoring | 70 | the failure of F9A is not reflected on CBS | Hardware | No | N/A | changing of lighting ballast |  | 21-02-2023 | 01:00:00 | 21-02-2023 | 02:10:00
L4-4C1-00019 | CCTV | 4C1CCTV | 4 cameras need configuration CMIN-GL003 CMIN-CL101 CMIN-CL102 |  | 09-10-2022 | 08:00:11 | Alarm indicated in Scada/ISM System | 120 | 4 cameras need configuration CMIN-GL003 CMIN-CL101 CMIN-CL102 | Software | No | N/A | Informed ICT team to rectify offline CCTV & configuration of CCTV |  | 21-02-2023 | 08:00:00 | 21-02-2023 | 10:00:00
L4-4B1-00023 | FCU | 4B1FCU | FCU Filters showing dirty |  | 30-01-2023 | 08:00:23 | Alarm idicated from SCADA/BMS System | 420 | FCU Filters showing dirty | Hardware | No | N/A | Cleaned the Filters by Site Team |  | 21-02-2023 | 08:00:00 | 21-02-2023 | 15:00:00
L4-4B1-00024 | FDS | 4B1FDS | Maintenace alart for Dirty |  | 12-02-2023 | 08:00:24 | Alarm idicated from SCADA/BMS System | 960 | Maintenace alart for Dirty | Hardware | No | N/A | ELECTRICAL TEAM |  | 21-02-2023 | 01:00:00 | 21-02-2023 | 17:00:00
L4-4E1-00037 | FCU | 4E1FCU | Blower motor bearing damaged FCU-4E1-CL-006 |  | 18-01-2023 | 08:01:54 | Physical inspection lead to the failure identification | 60 | Blower motor bearing damaged FCU-4E1-CL-006 | Hardware | No | N/A | Raised Pr for supplier |  | 21-09-2021 | 08:00:00 | 21-09-2021 | 09:00:00
L4-4G1-00017 | FCU | 4G1FCU | FCU-4G1-CL-014,12,25,28,26,29,09PL-01,01A,02,05,06,07 FCU's when running at low & medium speed no noice, but when running at high speed there is sound from FCU, which need to check by supplier |  | 16-08-2022 | 08:02:22 | Monitoring from SCADA/ BMS | 180 | FCU-4G1-CL-014,12,25,28,26,29,09PL-01,01A,02,05,06,07 FCU's when running at low & medium speed no noice, but when running at high speed there is sound from FCU, which need to check by supplier | Hardware | No | N/A | PR Raised for supplier |  | 21-09-2021 | 08:00:00 | 21-09-2021 | 11:00:00
L4-4C1-00029 | CCTV | 4C1CCTV | Image not appearing in camera CMIN-GL-001 |  | 09-10-2022 | 08:00:13 | Alarm indicated in Scada/ISM System | 180 | Image not appearing in camera CMIN-GL-001 | Software | No | N/A | Informed ICT team to rectify |  | 21-11-2022 | 08:00:00 | 21-11-2022 | 11:00:00
L4-4C2-00002 | CCTV | 4C2CCTV | CFIX-CL-003 CFIX-GL-11 CMIN-GL-09 CMIN-CL-011 Communication failure |  | 11-02-2023 | 08:00:23 | BMS and SCADA alarms. | 60 | CFIX-CL-003 CFIX-GL-11 CMIN-GL-09 CMIN-CL-011 Communication failure | Software | No | N/A | Informed ICT team to rectify |  | 21-11-2022 | 08:00:00 | 21-11-2022 | 09:00:00
L4-4B1-00008 | CWS | 4B1CWS | Made turn off due to additional - Chemical Dosing and Filtration unit is also OFF |  | 18-02-2023 | 08:00:08 | Alarms not indicated in SCADA/BMS system lead to physical inspection of failure indentification | 60 | Made turn off due to additional - Chemical Dosing and Filtration unit is also OFF | Hardware | No | N/A | PR raised for chemical and will deliver mid of february |  | 21-11-2022 | 08:00:00 | 21-11-2022 | 09:00:00
L4-4C1-00001 | CWS | 4C1CWS | Leaking from Chilled water pumps - CHWP-4C1-CL-004 |  | 30-01-2023 | 08:00:28 | Physical inspection lead to the failure identification | 60 | Leaking from Chilled water pumps - CHWP-4C1-CL-004 | Hardware | No | N/A | Raised PR and invite supplier to repair the mechanical seal |  | 21-11-2022 | 08:00:00 | 21-11-2022 | 09:00:00
L4-4C1-00003 | CWS | 4C1CWS | Made turn off due to addition of chemical -Water Softer , chemical dosing units also made Off in con 1 and 2 |  | 01-02-2023 | 08:00:30 | Physical inspection lead to the failure identification | 60 | Made turn off due to addition of chemical -Water Softer , chemical dosing units also made Off in con 1 and 2 | Hardware | No | N/A | PR raised for chemical and will deliver mid of february |  | 21-11-2022 | 08:00:00 | 21-11-2022 | 09:00:00
L4-4D1-00018 | CWS | 4D1CWS | Turned OFF |  | 06-02-2023 | 08:01:14 | Physical inspection lead to the failure identification | 120 | Turned OFF | Software | No | N/A | Waiting for delivery of chemical |  | 21-11-2022 | 08:00:00 | 21-11-2022 | 10:00:00
L4-4E1-00029 | CWS | 4E1CWS | Turned OFF |  | 04-01-2023 | 08:01:46 | Physical inspection lead to the failure identification | 60 | Turned OFF | Hardware | No | N/A | Waiting for delivery of chemical |  | 21-11-2022 | 08:00:00 | 21-11-2022 | 09:00:00
L4-4D1-00007 | ES | 4D1ES | OTIS Turned OFF from ESM System ECP2,ECP3,ECP4,ECP9,ECP10,ECP11,ECP12 |  | 09-03-2023 | 08:00:36 | Found during Physical Inspection | 90 | OTIS Turned OFF from ESM System ECP2,ECP3,ECP4,ECP9,ECP10,ECP11,ECP12 | Software | No | N/A | OTIS team Turned ON |  | 22-01-2023 | 08:30:00 | 22-01-2023 | 10:00:00
L4-4E1-00010 | FDS | 4E1FDS | Smoke detector fault at Ent 1, Ret room (L3-EL-Z5B-SMKE D04) |  | 16-01-2023 | 08:01:27 | Found alarm in FACP, lead to inspection of failure identification | 540 | Smoke detector fault at Ent 1, Ret room (L3-EL-Z5B-SMKE D04) | Software | No | N/A | Replaced smoke detector |  | 22-01-2023 | 07:00:00 | 22-01-2023 | 16:00:00
L6-6D2-0016 | LDP | 6D2LDP | all lighting connected to this module are not probably functinol |  | 04-10-2022 | 08:02:54 | Physical inspection lead to the failure identification | 68 | all lighting connected to this module are not probably functinol | Hardware | No | N/A | Requested from specialist supplier to change a module |  | 22-01-2023 | 08:30:00 | 22-01-2023 | 09:38:00
L4-4D1-00006 | LIFT | 4D1LIFT | OTIS Turned OFF from ESM System LCP2,LCP5,LCP6,LCP7,LCP8 |  | 09-03-2023 | 08:00:50 | Found during Physical Inspection | 30 | OTIS Turned OFF from ESM System LCP2,LCP5,LCP6,LCP7,LCP8 | Software | No | N/A | OTIS team Turned ON |  | 22-01-2023 | 08:30:00 | 22-01-2023 | 09:00:00
L4-4G1-00006 | TELEPHONE | 4G1TELEPHONE | Telecom landline |  | 31-05-2021 | 08:00:39 | Monitoring from SCADA/ACID System | 480 | Telecom landline | Software | No | N/A | informed ICT TEAM |  | 22-01-2023 | 08:00:00 | 22-01-2023 | 16:00:00
L6-6H1-0034 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 21-01-2023 | 08:05:34 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 22-01-2023 | 14:00:00 | 22-01-2023 | 14:30:00
L6-6G1-0024 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 06-02-2023 | 08:04:19 | during daily checking of UPS it was observed in (alarms Log) | 18.2667 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 22-02-2022 | 22:58:00 | 22-02-2022 | 23:16
L4-4E1-00032 | CCTV | 4E1CCTV | Online in ISM but no image/video appears. - CMIN-4E1-CL-04 |  | 09-10-2022 | 08:00:21 | Physical inspection lead to the failure identification | 420 | Online in ISM but no image/video appears. - CMIN-4E1-CL-04 | Software | No | N/A | Informed ICT team to rectify |  | 22-03-2023 | 10:00:00 | 22-03-2023 | 17:00:00
L4-4E1-00033 | CCTV | 4E1CCTV | CCTV image not clear - CMIP-4E1-CL-01 |  | 07-02-2023 | 08:00:22 | Physical inspection lead to the failure identification | 420 | CCTV image not clear - CMIP-4E1-CL-01 | Hardware | No | N/A | Informed ICT team to rectify |  | 22-03-2023 | 10:00:00 | 22-03-2023 | 17:00:00
L4-4D1-00008 | GEN | 4D1GEN | LPS Main Incomming Off from TSY |  | 08-12-2022 | 08:01:04 | Found during Physical Inspection | 60 | LPS Main Incomming Off from TSY | Hardware | No | N/A | Panel Rectified and Normal Power is ON |  | 23-01-2023 | 10:00:00 | 23-01-2023 | 11:00
L6-6H1-0035 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 24-01-2023 | 08:05:35 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 23-01-2023 | 15:00:00 | 23-01-2023 | 15:30:00
L6-6G1-0025 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 07-01-2023 | 08:04:20 | during daily checking of UPS it was observed in (alarms Log) | 16.2833 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 23-02-2022 | 23:04 | 23-02-2022 | 23:20
L4-4G1-00014 | FCU | 4G1FCU | AIR Flow issue |  | 22-06-2021 | 08:02:19 | Monitoring from SCADA/ BMS | 300 | AIR Flow issue | Hardware | No | N/A | Replaced Fan Motor |  | 23-02-2023 | 09:00:00 | 23-02-2023 | 14:00:00
L6-6H1-0036 | UPS | 6H1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 27-01-2023 | 08:05:36 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 24-01-2023 | 16:00:00 | 24-01-2023 | 16:30:00
L6-6G1-0026 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 16-01-2023 | 08:04:21 | during daily checking of UPS it was observed in (alarms Log) | 422.3 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 24-02-2022 | 00:58:00 | 24-02-2022 | 08:00:18
L4-4E1-00023 | CCTV | 4E1CCTV | 4 CCTV is offline in ISM system, Checked by ICT team from IP CCTv's are Online. Required TSY to rectify - L4E1-CMIN-CL-13, - L4E1-CMIN-GL-109, - L4E1-CMIN-GL-110 |  | 04-01-2023 | 08:00:19 | Found alarm in SCADA. Comapred ISM & scada | 180 | 4 CCTV is offline in ISM system, Checked by ICT team from IP CCTv's are Online. Required TSY to rectify - L4E1-CMIN-CL-13, - L4E1-CMIN-GL-109, - L4E1-CMIN-GL-110 | Software | No | N/A | Informed ICT team to coordibate with TSY |  | 24-11-2022 | 08:00:00 | 24-11-2022 | 11:00:00
L4-4E1-00024 | CCTV | 4E1CCTV | CCTV is offline in ISM system, Checked by ICT team from IP CCTv's are Online. Required TSY to rectify |  | 18-10-2022 | 08:00:20 | Found alarm in SCADA. Comapred ISM & scada | 180 | CCTV is offline in ISM system, Checked by ICT team from IP CCTv's are Online. Required TSY to rectify | Software | No | N/A | Informed ICT team to coordibate with TSY |  | 24-11-2022 | 08:00:00 | 24-11-2022 | 11:00:00
L4-4D1-00013 | CWS | 4D1CWS | Chilled water pump(CHP-4D1-CL-005) Damaged |  | 12-03-2023 | 08:01:09 | Found during Physical Inspection | 60 | Chilled water pump(CHP-4D1-CL-005) Damaged | Hardware | No | N/A | PR raised for maintenance |  | 24-11-2022 | 08:00:00 | 24-11-2022 | 09:00:00
L6-6F1-0013 | FOMSS | 6F1FOMSS | Gate Valve tamper switch Failure |  | 30-01-2023 | 08:03:42 | during fire scenario test there are no alarm on fire alarm panel | 180 | Gate Valve tamper switch Failure | Hardware | Yes | SRIL_CJV_083 | reported by supplier and ETECHS rectified |  | 24-12-2022 | 08:00:00 | 24-12-2022 | 11:00:00
L6-6D2-0009 | UPS | 6D2UPS | 6D2 UPS Interruption due to unstable incoming power from MV Source (UPS Rectifier Out of Tolerance) |  | 13-07-2022 | 08:02:47 | SMDBU Outgoing at 6D2 tripped due which the third rail power tripped. | 10 | 6D2 UPS Interruption due to unstable incoming power from MV Source (UPS Rectifier Out of Tolerance) | Hardware | No | N/A | UPS power restored |  | 25-01-2022 | 08:43:00 | 2022-01-25 | 08:53:00
L4-4G1-00007 | FDS | 4G1FDS | Flash alarm Beacons fault ES-27 Set to fault due to CH Device trouble |  | 15-11-2021 | 08:02:12 | Monitoring from SCADA/ Fire Alarm PANEL | 420 | Flash alarm Beacons fault ES-27 Set to fault due to CH Device trouble | Hardware | No | N/A | replaced CRH |  | 25-01-2023 | 07:00:00 | 25-01-2023 | 14:00:00
L4-4G1-00008 | FDS | 4G1FDS | Flash alarm Beacons fault ES-27 Set to fault due to CH Device trouble Smoke detector activate due to dust |  | 17-11-2021 | 08:02:13 | Monitoring from SCADA/ Fire Alarm PANEL | 240 | Flash alarm Beacons fault ES-27 Set to fault due to CH Device trouble Smoke detector activate due to dust | Hardware | No | N/A | device cleaned |  | 25-01-2023 | 08:00:00 | 25-01-2023 | 12:00:00
L4-4G1-00009 | FDS | 4G1FDS | Flash alarm Beacons fault ES-26 Set to fault due to CH Device trouble |  | 17-11-2021 | 08:02:14 | Monitoring from SCADA/ Fire Alarm PANEL | 240 | Flash alarm Beacons fault ES-26 Set to fault due to CH Device trouble | Hardware | No | N/A | device cleaned |  | 25-01-2023 | 09:00:00 | 25-01-2023 | 13:00:00
L4-4G1-00010 | FDS | 4G1FDS | Flash alarm Beacons fault ES-27 Set to fault due to Device trouble Smoke detector activate due to dust |  | 17-08-2021 | 08:02:15 | Monitoring from SCADA/ Fire Alarm PANEL | 240 | Flash alarm Beacons fault ES-27 Set to fault due to Device trouble Smoke detector activate due to dust | Hardware | No | N/A | device cleaned |  | 25-01-2023 | 10:00:00 | 25-01-2023 | 14:00:00
L4-4G1-00011 | FDS | 4G1FDS | Flash alarm Beacons fault VS-27 Set to fault due to CH Device trouble |  | 21-09-2021 | 08:02:16 | Monitoring from SCADA/ Fire Alarm PANEL | 240 | Flash alarm Beacons fault VS-27 Set to fault due to CH Device trouble | Hardware | No | N/A | device cleaned |  | 25-01-2023 | 10:00:00 | 25-01-2023 | 14:00:00
L4-4G1-00012 | FDS | 4G1FDS | Flash alarm Beacons fault VS-27 Set to fault due to CH Device trouble |  | 08-08-2022 | 08:02:17 | Monitoring from SCADA/ Fire Alarm PANEL | 240 | Flash alarm Beacons fault VS-27 Set to fault due to CH Device trouble | Hardware | No | N/A | device cleaned |  | 25-01-2023 | 10:00:00 | 25-01-2023 | 14:00:00
L6-6H2-0004 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 15-01-2023 | 08:05:41 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 25-01-2023 | 17:00:00 | 25-01-2023 | 17:30:00
L6-6G1-0027 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 06-12-2022 | 08:04:22 | during daily checking of UPS it was observed in (alarms Log) | 362.3167 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 25-02-2022 | 01:58:00 | 25-02-2022 | 08:00:19
L4-4E1-00026 | ACID | 4E1ACID | Door lock hardware issue - AC-4E1-BL-003 - AC-4E1-GL-001 - AC-4E1-CL-012 |  | 02-01-2023 | 08:00:33 | Found alarm in ACID, lead to inspection of failure identification | 540 | Door lock hardware issue - AC-4E1-BL-003 - AC-4E1-GL-001 - AC-4E1-CL-012 | Hardware | No | N/A | Informed Archi team to rectify |  | 25-02-2023 | 07:00:00 | 25-02-2023 | 16:00:00
L4-4G1-00028 | AHUS | 4G1AHUS | FAHU- motor belt damage need to replace |  | 10-11-2022 | 08:02:33 | Monitoring from SCADA/ found damage on site | 120 | FAHU- motor belt damage need to replace | Hardware | No | N/A | Belt replaced |  | 25-02-2023 | 10:00:00 | 25-02-2023 | 12:00:00
L6-6D2-0027 | AHUS | 6D2AHUS | Belt damaged |  | 16-01-2023 | 08:03:05 | during daily cartaking activites | 30 | Belt damaged | Hardware | No | N/A | replaced the belt |  | 25-02-2023 | 13:30:00 | 25-02-2023 | 14:00:00
L4-4G1-00023 | DWS | 4G1DWS | Flush valve sensor not working FWC & MWC |  | 26-10-2022 | 08:02:28 | Found during physical inspection | 480 | Flush valve sensor not working FWC & MWC | Hardware | No | N/A | Mechanical Team |  | 25-02-2023 | 08:00:00 | 25-02-2023 | 16:00:00
L6-6H1-0009 | FCU | 6H1FCU | PLC board Failure |  | 20-01-2023 | 08:05:09 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 25-08-2022 | 09:00:00 | 2022-08-26 | 12:00:00
L4-4G1-00013 | LDP | 4G1LDP | MONITOR GENERAL FAULT (TMCS-Command issue) |  | 19-02-2023 | 08:02:18 | found in SCADA / TMCS PANEL | 60 | MONITOR GENERAL FAULT (TMCS-Command issue) | Hardware | No | N/A | Informed TMCS |  | 26-01-2023 | 13:00:00 | 26-01-2023 | 14:00:00
L6-6H2-0005 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 20-01-2023 | 08:05:42 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 26-01-2023 | 18:00:00 | 26-01-2023 | 18:30:00
L6-6G1-0028 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 11-10-2022 | 08:04:23 | during daily checking of UPS it was observed in (alarms Log) | 302.3333 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 26-02-2022 | 02:58:00 | 26-02-2022 | 08:00:20
L4-4D1-00010 | ACID | 4D1ACID | ACID Door(ACCL-007) Required Configuration |  | 16-01-2023 | 08:00:03 | Found in SCADA Alarms | 60 | ACID Door(ACCL-007) Required Configuration | Software | No | N/A | Informed ICT team to rectify acid door |  | 26-02-2023 | 13:30:00 | 26-02-2023 | 14:30:00
L6-6F1-0026 | AHUS | 6F1AHUS | Air Filter Damaged |  | 18-02-2023 | 08:03:55 | during daily cartaking activites | 60 | Air Filter Damaged | Hardware | No | N/A | replaced Air filter |  | 26-02-2023 | 13:30:00 | 26-02-2023 | 14:30:00
L4-4C2-00010 | CCTV | 4C2CCTV | CMIN-GL-09, CMIP-CL-11 CCTV Not working |  | 07-02-2023 | 08:00:24 | SCADA alarms. | 120 | CMIN-GL-09, CMIP-CL-11 CCTV Not working | Software | No | N/A | ICT team to check |  | 26-02-2023 | 08:00:00 | 26-02-2023 | 10:00:00
L6-6G2-0011 | FCU | 6G2FCU | PLC board Failure |  | 29-01-2023 | 08:04:39 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 26-07-2022 | 09:00:00 | 2022-07-26 | 12:00:00
L6-6D2-0005 | SEXF | 6D2SEXF | FAN MOTOR Failure |  | 30-08-2022 | 08:02:43 | The Motor Burned | 180 | FAN MOTOR Failure | Hardware | No | N/A | rewind the motor |  | 26-09-2021 | 09:00:00 | 26-09-2021 | 12:00:00
L6-6G1-0009 | FCU | 6G1FCU | PLC & PCB board Failure |  | 12-02-2023 | 08:04:04 | The PCB & PCB board Burned | 180 | PLC & PCB board Failure | Hardware | No | N/A | PLC & PCB board replaced |  | 26-10-2022 | 08:00:00 | 26-10-2022 | 11:00:00
L6-6H2-0006 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 21-01-2023 | 08:05:43 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 27-01-2023 | 19:00:00 | 27-01-2023 | 19:30:00
L6-6G1-0029 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 07-12-2022 | 08:04:24 | during daily checking of UPS it was observed in (alarms Log) | 242.35 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 27-02-2022 | 03:58:00 | 27-02-2022 | 08:00:21
L6-6E1-0024 | CWS | 6E1CWS | the bearing Failure |  | 30-01-2023 | 08:03:29 | during daily cartaking activites overheat and noise of pump | 300 | the bearing Failure | Hardware | No | N/A | replaced the bearing |  | 27-02-2023 | 10:30:00 | 27-02-2023 | 15:30:00
L4-4D1-00012 | INTERCOM | 4D1INTERCOM | 01 Intercom(INT-CL-016) Required Configuration |  | 16-05-2022 | 08:00:44 | Found in SCADA Alarms | 450 | 01 Intercom(INT-CL-016) Required Configuration | Software | No | N/A | Informed ICT team to configure intercom |  | 27-02-2023 | 08:00:00 | 27-02-2023 | 15:30:00
L6-6E1-0001 | SEXF | 6E1SEXF | FAN MOTOR Failure |  | 22-01-2023 | 08:03:06 | The Motor Burned | 180 | FAN MOTOR Failure | Hardware | No | N/A | rewind the motor |  | 27-04-2021 | 08:00:00 | 27-04-2021 | 11:00:00
L6-6H2-0007 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 24-01-2023 | 08:05:44 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 28-01-2023 | 20:00:00 | 28-01-2023 | 20:30:00
L6-6G1-0030 | UPS | 6G1UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2022 | 08:04:25 | during daily checking of UPS it was observed in (alarms Log) | 182.3667 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 28-02-2022 | 04:58:00 | 28-02-2022 | 08:00:22
L4-4C2-00011 | ACID | 4C2ACID | Doors not working with access card AC-4C2-PL-004 |  | 21-02-2023 | 08:00:27 | SCADA alarms. | 60 | Doors not working with access card AC-4C2-PL-004 | Software | No | N/A | ICT team to check |  | 28-02-2023 | 10:00:00 | 28-02-2023 | 11:00:00
L4-4E1-00015 | CCTV | 4E1CCTV | CCTV image not clear |  | 15-09-2021 | 08:00:17 | Physical inspection lead to the failure identification | 120 | CCTV image not clear | Hardware | No | N/A | Informed ICT team to rectify |  | 28-02-2023 | 13:00:00 | 28-02-2023 | 15:00:00
L4-4E1-00005 | CHILLER | 4E1CHILLER | Expansion valve damaged |  | 07-01-2023 | 08:01:22 | Chiller not working, upon further investigation with supplier found expansion valve damaged | 120 | Expansion valve damaged | Hardware | No | N/A | PR Raised for replacement of expansion valve |  | 28-02-2023 | 13:00:00 | 28-02-2023 | 15:00:00
L4-4D1-00015 | EWH | 4D1EWH | SSR Room water heater Damaged |  | 25-02-2023 | 08:01:11 | Found during Physical Inspection | 210 | SSR Room water heater Damaged | Hardware | No | N/A | PR raised for maintenance |  | 28-02-2023 | 08:00:00 | 28-02-2023 | 11:30:00
L4-4C2-00004 | LIFT | 4C2LIFT | Power off by OTIS Lift 2,3,5,6/ Es-06 |  | 07-03-2023 | 08:00:49 | BMS and SCADA alarms. | 60 | Power off by OTIS Lift 2,3,5,6/ Es-06 | Hardware | No | N/A | To be power on by OTIS |  | 28-02-2023 | 10:00:00 | 28-02-2023 | 11:00:00
L4-4G1-00031 | TMCS | 4G1TMCS | TMCS PLC COMMUNICATION FAILSURE WITH SCADA |  | 06-02-2022 | 08:02:36 | found in SCADA / TMCS PANEL | 120 | TMCS PLC COMMUNICATION FAILSURE WITH SCADA | Software | No | N/A | Informed TMCS suplier |  | 28-02-2023 | 13:00:00 | 28-02-2023 | 15:00:00
L6-6H2-0008 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 27-01-2023 | 08:05:45 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 29-01-2023 | 21:00:00 | 29-01-2023 | 21:30:00
L6-6G1-0010 | FCU | 6G1FCU | The Transformer Failure |  | 12-02-2023 | 08:04:05 | The Transformer Burned | 180 | The Transformer Failure | Hardware | No | N/A | Transformer replaced |  | 29-10-2022 | 08:00:00 | 2022-10-29 | 11:00:00
L6-6G2-0018 | SEXF | 6G2SEXF | FAN MOTOR Failure |  | 27-01-2023 | 08:04:46 | The Motor Burned | 180 | FAN MOTOR Failure | Hardware | No | N/A | FAN REPLACED |  | 29-12-2022 | 08:00:00 | 29-12-2022 | 11:00:00
L6-6H2-0009 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 28-01-2023 | 08:05:46 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 30-01-2023 | 22:00:00 | 30-01-2023 | 22:30:00
L6-6G2-0012 | FCU | 6G2FCU | PLC board Failure |  | 30-01-2023 | 08:04:40 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 30-07-2022 | 09:00:00 | 2022-07-30 | 12:00:00
L6-C&C6.1-0001 | ACID | 6D2ACID | SIL2 sensor activated |  | 18-02-2023 | 08:00:56 | TSY-SCADA System | 17 | SIL2 sensor activated | Software | No |  | Switch on the switched off breaker |  | 31-01-2022 | 10:17:00 | 31-01-2022 | 10:34:00
L6-6D2-0017 | UPS | 6D2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 06-10-2022 | 08:02:55 | during daily checking of UPS it was observed in (alarms Log) | 79 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 2022-01-01 | 11:15:00 | 2022-01-01 | 12:34:00
L6-6H2-0010 | UPS | 6H2UPS | during daily checking of UPS in 6G1 it was observed in (alarms Log) |  | 31-01-2023 | 08:05:47 | during daily checking of UPS it was observed in (alarms Log) | 30 | during daily checking of UPS in 6G1 it was observed in (alarms Log) | Hardware | No | N/A | Auto normalized |  | 31-01-2023 | 23:00:00 | 31-01-2023 | 23:30:00
L6-6D2-0001 | FCU | 6D2FCU | PLC board Failure |  | 14-07-2022 | 08:02:39 | The PLC board malfunction | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 2021-05-21 | 08:00:00 | 2021-05-21 | 11:00:00
L6-6F1-0003 | UPS | 6F1UPS | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation |  | 28-02-2023 | 08:03:32 | all power off in the station | 120 | UPS rectifier (IGBT)and other internal components were damaged due to power fluctuation | Hardware | No | N/A | turned the UPS on manual by-pass |  | 31-08-2022 | 09:00:00 | 2022-08-31 | 11:00:00
L6-6F1-0009 | VRF | 6F1VRF | PLC board Failure |  | 09-02-2022 | 08:03:38 | indoor unit not working | 180 | PLC board Failure | Hardware | No | N/A | PLC board replaced |  | 31-10-2022 | 08:00:00 | 2022-10-31 | 11:00:00